## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 50 | 1 | 1 | 29 | 19 | 2.91 | 50 | 81.1 | 59.3 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 1 | 0 | 2 | 30 | 19.3 | 2.14 | 50 | 81.1 | 59.3 | 72.9 | 59.8 | 213.6 | 218.9 | 213.6 | YES
2 | OK | 0 | 2 | 2 | 30 | 19.3 | 2.14 | 50 | 81.1 | 59.3 | 72.9 | 59.3 | 213.6 | 219.2 | 213.6 | YES
3 | OK | 2 | 47 | 47 | 31 | 51.8 | 1.51 | 50 | 81.1 | 59.3 | 75.3 | 65.4 | 213.5 | 215.4 | 213.5 | YES
4 | OK | 47 | 48 | 48 | 31 | 93.6 | 0.36 | 50 | 81.1 | 59.3 | 79.7 | 60.7 | 213.5 | 218.3 | 213.5 | YES
5 | OK | 3 | 31 | 56 | 34 | 19.7 | 2.02 | 50 | 81.1 | 59.3 | 73 | 65.7 | 215.6 | 217.3 | 215.6 | YES
6 | OK | 48 | 49 | 49 | 31 | 96.6 | 0.36 | 50 | 81.1 | 59.3 | 79.7 | 60.7 | 213.5 | 218.3 | 213.5 | YES
7 | OK | 31 | 32 | 56 | 34 | 19.7 | 1.47 | 50 | 81.1 | 59.3 | 75.2 | 64.7 | 215.3 | 217.6 | 215.3 | YES
8 | OK | 49 | 51 | 51 | 31 | 129.2 | 0.36 | 50 | 81.1 | 59.3 | 79.7 | 60.7 | 213.5 | 218.3 | 213.5 | YES
9 | OK | 22 | 23 | 23 | 26 | 35.8 | 1.3 | 50 | 81.1 | 59.3 | 75.8 | 60.9 | 215 | 218.5 | 215 | YES
10 | OK | 22 | 7 | 11 | 37 | 20.3 | 1.47 | 50 | 81.1 | 59.3 | 75.3 | 65 | 213.2 | 219.4 | 213.2 | YES
11 | OK | 32 | 45 | 56 | 34 | 19.7 | 1.37 | 50 | 81.1 | 59.3 | 75.6 | 64.7 | 215.4 | 217.6 | 215.4 | YES
12 | OK | 23 | 24 | 25 | 28 | 38.4 | 0.46 | 50 | 81.1 | 59.3 | 79.2 | 59.8 | 214.1 | 219 | 214.1 | YES
13 | OK | 7 | 8 | 11 | 37 | 20.3 | 1.09 | 50 | 81.1 | 59.3 | 76.8 | 63.5 | 213.3 | 219.4 | 213.3 | YES
14 | OK | 45 | 54 | 56 | 34 | 19.7 | 0.71 | 50 | 81.1 | 59.3 | 78.2 | 62.1 | 214.5 | 218.4 | 214.5 | YES
15 | OK | 8 | 11 | 11 | 37 | 20.3 | 0.49 | 50 | 81.1 | 59.3 | 79.2 | 61.2 | 213.4 | 219.3 | 213.4 | YES
16 | OK | 54 | 46 | 46 | 0 | 54.1 | 0.71 | 50 | 81.1 | 59.3 | 78.2 | 62 | 214.5 | 219.2 | 214.5 | YES
17 | OK | 39 | 10 | 12 | 4 | 25.8 | 3.99 | 50 | 81.1 | 59.3 | 64.9 | 75.5 | 220 | 212.2 | 212.2 | YES
18 | OK | 39 | 40 | 44 | 25 | 53.3 | 2.2 | 50 | 81.1 | 59.3 | 72.5 | 68.3 | 213.1 | 213.4 | 213.1 | YES
19 | OK | 39 | 26 | 26 | 33 | 51.7 | 3.71 | 50 | 81.1 | 59.3 | 62.5 | 74.4 | 220 | 211.7 | 211.7 | YES
20 | OK | 10 | 9 | 12 | 4 | 25.8 | 3.25 | 50 | 81.1 | 59.3 | 67.8 | 72.4 | 219.3 | 213.6 | 213.6 | YES
21 | OK | 40 | 35 | 44 | 25 | 53.3 | 0.97 | 50 | 81.1 | 59.3 | 77.3 | 63.2 | 213.3 | 216.8 | 213.3 | YES
22 | OK | 26 | 27 | 27 | 26 | 54.6 | 3.71 | 50 | 81.1 | 59.3 | 62.5 | 74.5 | 220 | 211.1 | 211.1 | YES
23 | ** OPTIMAL ** | 9 | 12 | 12 | 4 | 25.8 | 1.19 | 50 | 81.1 | 59.3 | 76.2 | 64 | 215.8 | 217.2 | 215.8 | YES
24 | OK | 35 | 36 | 44 | 25 | 53.3 | 0.97 | 50 | 81.1 | 59.3 | 77.3 | 63.2 | 213.3 | 216.8 | 213.3 | YES
25 | OK | 27 | 28 | 28 | 28 | 56.8 | 1.81 | 50 | 81.1 | 59.3 | 72.3 | 66.6 | 217.2 | 215.1 | 215.1 | YES
26 | OK | 12 | 16 | 16 | 15 | 36.5 | 0.4 | 50 | 81.1 | 59.3 | 79.4 | 60.9 | 214.4 | 218.4 | 214.4 | YES
27 | OK | 36 | 6 | 5 | 33 | 93 | 0.6 | 50 | 81.1 | 59.3 | 78.7 | 61.7 | 213.4 | 218.2 | 213.4 | YES
28 | OK | 36 | 41 | 44 | 25 | 53.3 | 0.37 | 50 | 81.1 | 59.3 | 79.6 | 60.7 | 213.4 | 218.4 | 213.4 | YES
29 | OK | 28 | 29 | 30 | 29 | 59.4 | 0.96 | 50 | 81.1 | 59.3 | 77.1 | 63.1 | 215.2 | 217 | 215.2 | YES
| NG | 6 | 5 | 5 | 33 | 93 | 0.6 | 50 | 81.1 | 59.3 | 78.7 | 9.7766e+128 | 213.4 | 2281055454697502 | 213.4 | NO
30 | OK | 41 | 42 | 44 | 25 | 53.3 | 0.37 | 50 | 81.1 | 59.3 | 79.6 | 59.3 | 213.4 | 219.2 | 213.4 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 65-009157
TR_B (available) | 45-002231
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 81.1
TR_B Baseline Loading% | 59.3
Total Scenarios Evaluated | 32
Feasible Scenarios | 30
--- Optimal Solution ---
Switch Parent Node | 9
Switch Child Node | 12
Tie Node (TR_A side) | 12
Tie Node (TR_B side) | 4
Tie Line Distance (m) | 25.8
Load Transferred (kW) | 1.19
TR_A Loading After (%) | 76.2
TR_B Loading After (%) | 64
Minimum Voltage (V) | 215.8