## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 13 | 12 | 9 | 8 | 46.6 | 8.87 | 50 | 81 | 6 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 12 | 4 | 9 | 8 | 46.6 | 7.74 | 50 | 81 | 6 | 51.2 | 37 | 224.9 | 211.7 | 211.7 | YES
2 | OK | 4 | 16 | 9 | 8 | 46.6 | 3.96 | 50 | 81 | 6 | 65.7 | 21.4 | 221.5 | 222.4 | 221.5 | YES
3 | OK | 16 | 7 | 9 | 8 | 46.6 | 3.96 | 50 | 81 | 6 | 65.7 | 21.4 | 221.5 | 222.4 | 221.5 | YES
4 | OK | 7 | 6 | 9 | 8 | 46.6 | 3.72 | 50 | 81 | 6 | 66.6 | 20.4 | 221.5 | 222.8 | 221.5 | YES
5 | OK | 6 | 5 | 9 | 8 | 46.6 | 3.72 | 50 | 81 | 6 | 66.6 | 18.7 | 221.5 | 223.7 | 221.5 | YES
6 | ** OPTIMAL ** | 5 | 15 | 9 | 8 | 46.6 | 3.28 | 50 | 81 | 6 | 68.3 | 18.7 | 221.5 | 223.7 | 221.5 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 65-009242
TR_B (available) | 66-007225
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 81
TR_B Baseline Loading% | 6
Total Scenarios Evaluated | 7
Feasible Scenarios | 6
--- Optimal Solution ---
Switch Parent Node | 5
Switch Child Node | 15
Tie Node (TR_A side) | 9
Tie Node (TR_B side) | 8
Tie Line Distance (m) | 46.6
Load Transferred (kW) | 3.28
TR_A Loading After (%) | 68.3
TR_B Loading After (%) | 18.7
Minimum Voltage (V) | 221.5