## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 6 | 5 | 29 | 50 | 4.6 | 16.99 | 50 | 98.1 | 37.2 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 6 | 7 | 36 | 19 | 4.3 | 8.24 | 50 | 98.1 | 37.2 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 5 | 4 | 29 | 50 | 4.6 | 16.04 | 50 | 98.1 | 37.2 | 35.1 | 46.6 | 225.6 | 212.8 | 212.8 | YES
2 | OK | 4 | 11 | 29 | 50 | 4.6 | 16.03 | 50 | 98.1 | 37.2 | 35.2 | 46.6 | 225.6 | 212.8 | 212.8 | YES
3 | OK | 11 | 14 | 29 | 50 | 4.6 | 16.03 | 50 | 98.1 | 37.2 | 35.2 | 46.6 | 225.6 | 212.8 | 212.8 | YES
4 | OK | 14 | 0 | 18 | 50 | 116.2 | 9.77 | 50 | 98.1 | 37.2 | 59.3 | 42.1 | 221.6 | 215.6 | 215.6 | YES
5 | OK | 0 | 1 | 18 | 50 | 116.2 | 7.92 | 50 | 98.1 | 37.2 | 66.5 | 42.1 | 220.9 | 215.6 | 215.6 | YES
6 | OK | 1 | 3 | 18 | 50 | 116.2 | 7.23 | 50 | 98.1 | 37.2 | 69.2 | 41.3 | 220.7 | 215.8 | 215.8 | YES
7 | OK | 3 | 15 | 18 | 50 | 116.2 | 7.23 | 50 | 98.1 | 37.2 | 69.2 | 41.3 | 220.7 | 215.8 | 215.8 | YES
8 | ** OPTIMAL ** | 15 | 16 | 18 | 50 | 116.2 | 6.02 | 50 | 98.1 | 37.2 | 74 | 41.1 | 219.5 | 215.8 | 215.8 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 65-009998
TR_B (available) | 66-015847
TR_A Rated kVA | 30
TR_B Rated kVA | 100
TR_A Baseline Loading% | 98.1
TR_B Baseline Loading% | 37.2
Total Scenarios Evaluated | 10
Feasible Scenarios | 8
--- Optimal Solution ---
Switch Parent Node | 15
Switch Child Node | 16
Tie Node (TR_A side) | 18
Tie Node (TR_B side) | 50
Tie Line Distance (m) | 116.2
Load Transferred (kW) | 6.02
TR_A Loading After (%) | 74
TR_B Loading After (%) | 41.1
Minimum Voltage (V) | 215.8