## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 3 | 11 | 23 | 16 | 157.6 | 10.43 | 50 | 94.9 | 30.5 | 53.4 | 72 | 216.9 | 210.2 | 210.2 | YES
2 | OK | 11 | 12 | 23 | 16 | 157.6 | 9.29 | 50 | 94.9 | 30.5 | 57.8 | 67.3 | 215.8 | 212.3 | 212.3 | YES
3 | ** OPTIMAL ** | 12 | 10 | 23 | 16 | 157.6 | 8.91 | 50 | 94.9 | 30.5 | 59.3 | 64.6 | 215.4 | 213.5 | 213.5 | YES
4 | OK | 10 | 8 | 23 | 16 | 157.6 | 8.64 | 50 | 94.9 | 30.5 | 60.3 | 64.6 | 215.2 | 213.5 | 213.5 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 65-011160
TR_B (available) | 50-007039
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 94.9
TR_B Baseline Loading% | 30.5
Total Scenarios Evaluated | 4
Feasible Scenarios | 4
--- Optimal Solution ---
Switch Parent Node | 12
Switch Child Node | 10
Tie Node (TR_A side) | 23
Tie Node (TR_B side) | 16
Tie Line Distance (m) | 157.6
Load Transferred (kW) | 8.91
TR_A Loading After (%) | 59.3
TR_B Loading After (%) | 64.6
Minimum Voltage (V) | 213.5