## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 18 | 17 | 52 | 27 | 38.9 | 11.98 | 50 | 83.1 | 46.7 | 35.8 | 75.4 | 220.4 | 209.5 | 209.5 | NO
1 | OK | 17 | 16 | 52 | 27 | 38.9 | 11.77 | 50 | 83.1 | 46.7 | 36.6 | 74.9 | 220.3 | 210.1 | 210.1 | YES
2 | OK | 16 | 15 | 52 | 27 | 38.9 | 11.45 | 50 | 83.1 | 46.7 | 37.8 | 74.1 | 220.1 | 211.2 | 211.2 | YES
3 | OK | 15 | 14 | 52 | 27 | 38.9 | 11.45 | 50 | 83.1 | 46.7 | 37.8 | 74.1 | 220.1 | 211.2 | 211.2 | YES
4 | OK | 14 | 34 | 52 | 27 | 38.9 | 11.45 | 50 | 83.1 | 46.7 | 37.8 | 74.1 | 220.1 | 211.2 | 211.2 | YES
5 | OK | 34 | 33 | 52 | 27 | 38.9 | 11.22 | 50 | 83.1 | 46.7 | 38.7 | 73.5 | 219.9 | 211.9 | 211.9 | YES
6 | OK | 33 | 32 | 52 | 27 | 38.9 | 10.86 | 50 | 83.1 | 46.7 | 40.1 | 72.6 | 219.6 | 213.1 | 213.1 | YES
7 | OK | 32 | 25 | 52 | 27 | 38.9 | 10.7 | 50 | 83.1 | 46.7 | 40.7 | 72.2 | 219.5 | 213.2 | 213.2 | YES
8 | OK | 25 | 29 | 52 | 27 | 38.9 | 9 | 50 | 83.1 | 46.7 | 47.3 | 68.1 | 218.2 | 213 | 213 | YES
9 | OK | 29 | 28 | 52 | 27 | 38.9 | 8.73 | 50 | 83.1 | 46.7 | 48.3 | 67.5 | 218 | 212.9 | 212.9 | YES
10 | OK | 28 | 54 | 52 | 27 | 38.9 | 8.42 | 50 | 83.1 | 46.7 | 49.5 | 66.7 | 217.8 | 212.7 | 212.7 | YES
11 | OK | 54 | 27 | 52 | 27 | 38.9 | 7.74 | 50 | 83.1 | 46.7 | 52.1 | 65 | 217.8 | 214.3 | 214.3 | YES
12 | OK | 27 | 23 | 52 | 27 | 38.9 | 3.94 | 50 | 83.1 | 46.7 | 67.1 | 55.8 | 217.2 | 214.8 | 214.8 | YES
13 | ** OPTIMAL ** | 27 | 12 | 12 | 35 | 39.1 | 3.8 | 50 | 83.1 | 46.7 | 67.6 | 55.4 | 215.4 | 215.5 | 215.4 | YES
14 | OK | 23 | 24 | 52 | 27 | 38.9 | 3.12 | 50 | 83.1 | 46.7 | 70.4 | 53.9 | 216.6 | 215.2 | 215.2 | YES
15 | OK | 12 | 13 | 13 | 35 | 50.9 | 3 | 50 | 83.1 | 46.7 | 70.5 | 53.6 | 213.5 | 215.9 | 213.5 | YES
16 | OK | 24 | 21 | 52 | 27 | 38.9 | 3.09 | 50 | 83.1 | 46.7 | 70.5 | 52.3 | 216.6 | 215.3 | 215.3 | YES
17 | OK | 13 | 30 | 30 | 2 | 90.4 | 3 | 50 | 83.1 | 46.7 | 70.9 | 53.6 | 213.5 | 215.9 | 213.5 | YES
18 | OK | 21 | 22 | 52 | 27 | 38.9 | 1.57 | 50 | 83.1 | 46.7 | 76.7 | 50.3 | 215.4 | 215.2 | 215.2 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 65-013195
TR_B (available) | 56-013767
TR_A Rated kVA | 30
TR_B Rated kVA | 50
TR_A Baseline Loading% | 83.1
TR_B Baseline Loading% | 46.7
Total Scenarios Evaluated | 19
Feasible Scenarios | 18
--- Optimal Solution ---
Switch Parent Node | 27
Switch Child Node | 12
Tie Node (TR_A side) | 12
Tie Node (TR_B side) | 35
Tie Line Distance (m) | 39.1
Load Transferred (kW) | 3.8
TR_A Loading After (%) | 67.6
TR_B Loading After (%) | 55.4
Minimum Voltage (V) | 215.4