## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 26 | 12 | 6 | 14 | 5.9 | 2.88 | 50 | 43.7 | 56.6 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 12 | 11 | 6 | 14 | 5.9 | 2.88 | 50 | 43.7 | 56.6 | 37.1 | 59.9 | 213.8 | 216.8 | 213.8 | YES
2 | OK | 11 | 28 | 6 | 14 | 5.9 | 2.88 | 50 | 43.7 | 56.6 | 37.1 | 59.9 | 213.8 | 216.8 | 213.8 | YES
3 | ** OPTIMAL ** | 28 | 24 | 6 | 14 | 5.9 | 2.88 | 50 | 43.7 | 56.6 | 37.1 | 59.9 | 213.8 | 216.8 | 213.8 | YES
4 | OK | 24 | 22 | 6 | 14 | 5.9 | 2.24 | 50 | 43.7 | 56.6 | 38.6 | 59.9 | 213.5 | 216.8 | 213.5 | YES
5 | OK | 22 | 21 | 6 | 14 | 5.9 | 2.24 | 50 | 43.7 | 56.6 | 38.6 | 59.9 | 213.5 | 216.8 | 213.5 | YES
6 | OK | 21 | 20 | 6 | 14 | 5.9 | 2.24 | 50 | 43.7 | 56.6 | 38.6 | 59.9 | 213.5 | 216.8 | 213.5 | YES
7 | OK | 20 | 7 | 6 | 14 | 5.9 | 1.61 | 50 | 43.7 | 56.6 | 40 | 59.9 | 213.5 | 216.8 | 213.5 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 65-014951
TR_B (available) | 61-003969
TR_A Rated kVA | 50
TR_B Rated kVA | 30
TR_A Baseline Loading% | 43.7
TR_B Baseline Loading% | 56.6
Total Scenarios Evaluated | 8
Feasible Scenarios | 7
--- Optimal Solution ---
Switch Parent Node | 28
Switch Child Node | 24
Tie Node (TR_A side) | 6
Tie Node (TR_B side) | 14
Tie Line Distance (m) | 5.9
Load Transferred (kW) | 2.88
TR_A Loading After (%) | 37.1
TR_B Loading After (%) | 59.9
Minimum Voltage (V) | 213.8