## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 26 | 27 | 1 | 57 | 2 | 15.74 | 50 | 43.7 | 39 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 27 | 29 | 1 | 57 | 2 | 15.74 | 50 | 43.7 | 39 | 6.6 | 50.6 | 229.4 | 218.8 | 218.8 | YES
2 | OK | 29 | 25 | 1 | 57 | 2 | 15.74 | 50 | 43.7 | 39 | 6.6 | 50.6 | 229.4 | 218.8 | 218.8 | YES
3 | OK | 25 | 10 | 1 | 57 | 2 | 15.74 | 50 | 43.7 | 39 | 6.6 | 50.6 | 229.4 | 218.8 | 218.8 | YES
4 | OK | 10 | 9 | 1 | 57 | 2 | 15.21 | 50 | 43.7 | 39 | 7.8 | 50.3 | 229.4 | 218.8 | 218.8 | YES
5 | OK | 9 | 8 | 1 | 57 | 2 | 14.03 | 50 | 43.7 | 39 | 10.5 | 49.4 | 229.1 | 218.8 | 218.8 | YES
6 | OK | 8 | 2 | 1 | 57 | 2 | 13.19 | 50 | 43.7 | 39 | 12.4 | 48.8 | 228.5 | 218.8 | 218.8 | YES
7 | OK | 2 | 3 | 1 | 57 | 2 | 10.24 | 50 | 43.7 | 39 | 19.2 | 46.6 | 227.9 | 218.2 | 218.2 | YES
8 | OK | 3 | 23 | 1 | 57 | 2 | 9.89 | 50 | 43.7 | 39 | 20 | 46.4 | 227.5 | 218.1 | 218.1 | YES
9 | OK | 23 | 14 | 1 | 57 | 2 | 9.89 | 50 | 43.7 | 39 | 20 | 46.4 | 227.5 | 218.1 | 218.1 | YES
10 | OK | 14 | 15 | 1 | 57 | 2 | 9.86 | 50 | 43.7 | 39 | 20.1 | 46.3 | 227.5 | 218.1 | 218.1 | YES
11 | OK | 15 | 13 | 1 | 57 | 2 | 8.68 | 50 | 43.7 | 39 | 22.9 | 45.5 | 225.7 | 217.9 | 217.9 | YES
12 | OK | 13 | 0 | 1 | 57 | 2 | 8.02 | 50 | 43.7 | 39 | 24.4 | 45 | 225.6 | 217.9 | 217.9 | YES
13 | OK | 0 | 1 | 1 | 57 | 2 | 7.99 | 50 | 43.7 | 39 | 24.5 | 45 | 225.6 | 217.9 | 217.9 | YES
14 | OK | 1 | 4 | 4 | 57 | 31.7 | 7.99 | 50 | 43.7 | 39 | 24.5 | 45 | 225.6 | 217.9 | 217.9 | YES
15 | OK | 4 | 5 | 5 | 57 | 73.9 | 7.23 | 50 | 43.7 | 39 | 26.2 | 44.4 | 225.6 | 218.6 | 218.6 | YES
16 | ** OPTIMAL ** | 5 | 16 | 16 | 57 | 98.4 | 5.41 | 50 | 43.7 | 39 | 30.4 | 43 | 225.8 | 220.4 | 220.4 | YES
17 | OK | 16 | 17 | 19 | 28 | 106.3 | 3.48 | 50 | 43.7 | 39 | 35 | 41.7 | 222.3 | 217.9 | 217.9 | YES
18 | OK | 17 | 18 | 18 | 28 | 126.1 | 3.48 | 50 | 43.7 | 39 | 35 | 41.7 | 222.3 | 218.4 | 218.4 | YES
19 | OK | 18 | 30 | 30 | 46 | 146.3 | 3.43 | 50 | 43.7 | 39 | 35.1 | 41.6 | 222.2 | 217 | 217 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 65-014951
TR_B (available) | 67-029320
TR_A Rated kVA | 50
TR_B Rated kVA | 160
TR_A Baseline Loading% | 43.7
TR_B Baseline Loading% | 39
Total Scenarios Evaluated | 20
Feasible Scenarios | 19
--- Optimal Solution ---
Switch Parent Node | 5
Switch Child Node | 16
Tie Node (TR_A side) | 16
Tie Node (TR_B side) | 57
Tie Line Distance (m) | 98.4
Load Transferred (kW) | 5.41
TR_A Loading After (%) | 30.4
TR_B Loading After (%) | 43
Minimum Voltage (V) | 220.4