## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 5 | 6 | 3 | 33 | 9.8 | 23.93 | 50 | 99 | 10.9 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 6 | 7 | 3 | 33 | 9.8 | 21.36 | 50 | 99 | 10.9 | 14.9 | 39.1 | 228.7 | 191.1 | 191.1 | NO
| NG | 7 | 2 | 3 | 33 | 9.8 | 21.25 | 50 | 99 | 10.9 | 15.3 | 38.9 | 228.7 | 191.3 | 191.3 | NO
| NG | 2 | 14 | 14 | 33 | 21.9 | 21.25 | 50 | 99 | 10.9 | 15.3 | 38.7 | 228.7 | 192.7 | 192.7 | NO
| NG | 14 | 15 | 15 | 33 | 55 | 20.21 | 50 | 99 | 10.9 | 19.3 | 37.1 | 228.7 | 194.8 | 194.8 | NO
| NG | 15 | 23 | 23 | 33 | 57.2 | 16.52 | 50 | 99 | 10.9 | 33.4 | 31.8 | 225.9 | 201.2 | 201.2 | NO
1 | ** OPTIMAL ** | 23 | 16 | 21 | 25 | 75.5 | 7.97 | 50 | 99 | 10.9 | 67.2 | 10.9 | 215.1 | 224.3 | 215.1 | YES
2 | OK | 16 | 8 | 21 | 25 | 75.5 | 6.46 | 50 | 99 | 10.9 | 73.4 | 10.9 | 212.9 | 224.3 | 212.9 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 65-016029
TR_B (available) | 24-015685
TR_A Rated kVA | 30
TR_B Rated kVA | 100
TR_A Baseline Loading% | 99
TR_B Baseline Loading% | 10.9
Total Scenarios Evaluated | 8
Feasible Scenarios | 2
--- Optimal Solution ---
Switch Parent Node | 23
Switch Child Node | 16
Tie Node (TR_A side) | 21
Tie Node (TR_B side) | 25
Tie Line Distance (m) | 75.5
Load Transferred (kW) | 7.97
TR_A Loading After (%) | 67.2
TR_B Loading After (%) | 10.9
Minimum Voltage (V) | 215.1