## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 5 | 6 | 3 | 6 | 8.1 | 23.93 | 50 | 99 | 37.8 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 6 | 7 | 3 | 6 | 8.1 | 21.36 | 50 | 99 | 37.8 | 14.9 | 64.9 | 228.7 | 199.8 | 199.8 | NO
| NG | 7 | 2 | 3 | 6 | 8.1 | 21.25 | 50 | 99 | 37.8 | 15.3 | 64.7 | 228.7 | 199.9 | 199.9 | NO
| NG | 2 | 14 | 14 | 6 | 24.5 | 21.25 | 50 | 99 | 37.8 | 15.3 | 64.6 | 228.7 | 200.7 | 200.7 | NO
| NG | 14 | 15 | 15 | 6 | 58.6 | 20.21 | 50 | 99 | 37.8 | 19.3 | 63.2 | 228.7 | 202.1 | 202.1 | NO
| NG | 15 | 23 | 23 | 6 | 60.8 | 16.52 | 50 | 99 | 37.8 | 33.4 | 58.3 | 225.9 | 206.4 | 206.4 | NO
1 | ** OPTIMAL ** | 23 | 16 | 16 | 6 | 92.2 | 7.97 | 50 | 99 | 37.8 | 67.2 | 47.4 | 215.1 | 215 | 215 | YES
2 | OK | 16 | 8 | 8 | 6 | 128.7 | 6.46 | 50 | 99 | 37.8 | 73.4 | 45.6 | 212.9 | 214.9 | 212.9 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 65-016029
TR_B (available) | 65-027058
TR_A Rated kVA | 30
TR_B Rated kVA | 100
TR_A Baseline Loading% | 99
TR_B Baseline Loading% | 37.8
Total Scenarios Evaluated | 8
Feasible Scenarios | 2
--- Optimal Solution ---
Switch Parent Node | 23
Switch Child Node | 16
Tie Node (TR_A side) | 16
Tie Node (TR_B side) | 6
Tie Line Distance (m) | 92.2
Load Transferred (kW) | 7.97
TR_A Loading After (%) | 67.2
TR_B Loading After (%) | 47.4
Minimum Voltage (V) | 215