## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 6 | 5 | 17 | 32 | 2.9 | 7.11 | 50 | 81.3 | 52.2 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 5 | 3 | 17 | 32 | 2.9 | 7.11 | 50 | 81.3 | 52.2 | 54.1 | 80.4 | 219.8 | 214.7 | 214.7 | NO
1 | OK | 3 | 2 | 17 | 32 | 2.9 | 6.42 | 50 | 81.3 | 52.2 | 56.7 | 77.5 | 219.3 | 214.7 | 214.7 | YES
2 | OK | 3 | 4 | 4 | 45 | 3.1 | 0.69 | 50 | 81.3 | 52.2 | 78.6 | 54.8 | 217.3 | 214.7 | 214.7 | YES
3 | OK | 2 | 19 | 17 | 32 | 2.9 | 1.55 | 50 | 81.3 | 52.2 | 75.3 | 58.1 | 217.2 | 214.7 | 214.7 | YES
4 | OK | 2 | 0 | 0 | 41 | 3 | 4.87 | 50 | 81.3 | 52.2 | 62.6 | 71.3 | 218.8 | 214.7 | 214.7 | YES
5 | OK | 24 | 43 | 42 | 40 | 2.9 | 2.66 | 50 | 81.3 | 52.2 | 70.9 | 62.6 | 218.7 | 214.7 | 214.7 | YES
6 | OK | 0 | 1 | 20 | 42 | 3.2 | 4.25 | 50 | 81.3 | 52.2 | 65 | 68.8 | 218.4 | 214.7 | 214.7 | YES
7 | OK | 43 | 41 | 42 | 40 | 2.9 | 1.69 | 50 | 81.3 | 52.2 | 74.7 | 58.7 | 218.6 | 214.7 | 214.7 | YES
8 | OK | 1 | 20 | 20 | 42 | 3.2 | 2.4 | 50 | 81.3 | 52.2 | 72.1 | 61.5 | 217.6 | 214.7 | 214.7 | YES
| NG | 26 | 7 | 37 | 51 | 2 | 7.57 | 50 | 81.3 | 52.2 | 51.6 | 84.9 | 222.7 | 197.2 | 197.2 | NO
9 | OK | 7 | 8 | 30 | 52 | 2.8 | 1.31 | 50 | 81.3 | 52.2 | 76.1 | 57.3 | 217.8 | 214.7 | 214.7 | YES
| NG | 7 | 32 | 37 | 51 | 2 | 6.26 | 50 | 81.3 | 52.2 | 56.7 | 78.5 | 221.6 | 204.2 | 204.2 | NO
10 | OK | 8 | 27 | 30 | 52 | 2.8 | 1.31 | 50 | 81.3 | 52.2 | 76.1 | 57.3 | 217.8 | 214.7 | 214.7 | YES
| NG | 32 | 33 | 37 | 51 | 2 | 5.73 | 50 | 81.3 | 52.2 | 58.8 | 76.1 | 220.7 | 206.7 | 206.7 | NO
11 | OK | 27 | 28 | 30 | 52 | 2.8 | 0.45 | 50 | 81.3 | 52.2 | 79.5 | 53.9 | 217.1 | 214.7 | 214.7 | YES
| NG | 33 | 13 | 37 | 51 | 2 | 5.41 | 50 | 81.3 | 52.2 | 60 | 74.6 | 220.2 | 208.2 | 208.2 | NO
12 | OK | 13 | 14 | 14 | 34 | 3.4 | 2.37 | 50 | 81.3 | 52.2 | 71.9 | 61.4 | 216.5 | 214.7 | 214.7 | YES
13 | OK | 13 | 15 | 37 | 51 | 2 | 3.04 | 50 | 81.3 | 52.2 | 69.2 | 64.3 | 220.4 | 214.7 | 214.7 | YES
14 | OK | 14 | 34 | 34 | 34 | 3.5 | 1 | 50 | 81.3 | 52.2 | 77.3 | 53.6 | 216.7 | 214.7 | 214.7 | YES
15 | OK | 15 | 16 | 37 | 51 | 2 | 3.04 | 50 | 81.3 | 52.2 | 69.2 | 64.3 | 220.4 | 214.7 | 214.7 | YES
16 | OK | 16 | 35 | 37 | 51 | 2 | 2.76 | 50 | 81.3 | 52.2 | 70.3 | 63.1 | 219.8 | 214.7 | 214.7 | YES
17 | OK | 35 | 9 | 37 | 51 | 2 | 2.71 | 50 | 81.3 | 52.2 | 70.5 | 62.9 | 219.8 | 214.7 | 214.7 | YES
18 | OK | 9 | 10 | 37 | 51 | 2 | 1.08 | 50 | 81.3 | 52.2 | 77 | 56.4 | 218 | 214.7 | 214.7 | YES
19 | OK | 9 | 48 | 39 | 47 | 2.8 | 1.63 | 50 | 81.3 | 52.2 | 74.8 | 58.5 | 218.5 | 214.7 | 214.7 | YES
20 | OK | 48 | 39 | 39 | 47 | 2.8 | 1.63 | 50 | 81.3 | 52.2 | 74.8 | 58.5 | 218.5 | 214.7 | 214.7 | YES
21 | OK | 39 | 11 | 11 | 47 | 5.7 | 1.4 | 50 | 81.3 | 52.2 | 75.7 | 57.6 | 218.5 | 214.7 | 214.7 | YES
22 | OK | 11 | 12 | 12 | 47 | 12.3 | 1.4 | 50 | 81.3 | 52.2 | 75.7 | 57.6 | 218.5 | 214.7 | 214.7 | YES
23 | ** OPTIMAL ** | 12 | 40 | 40 | 47 | 14.2 | 0.72 | 50 | 81.3 | 52.2 | 78.4 | 52.2 | 218.6 | 214.7 | 214.7 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 65-016676
TR_B (available) | 63-019363
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 81.3
TR_B Baseline Loading% | 52.2
Total Scenarios Evaluated | 29
Feasible Scenarios | 23
--- Optimal Solution ---
Switch Parent Node | 12
Switch Child Node | 40
Tie Node (TR_A side) | 40
Tie Node (TR_B side) | 47
Tie Line Distance (m) | 14.2
Load Transferred (kW) | 0.72
TR_A Loading After (%) | 78.4
TR_B Loading After (%) | 52.2
Minimum Voltage (V) | 214.7