## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 51 | 52 | 74 | 77 | 72.9 | 24.16 | 50 | 68.5 | 12.1 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 52 | 53 | 74 | 77 | 72.9 | 22.51 | 50 | 68.5 | 12.1 | 40.5 | 17.8 | 223.8 | 180.9 | 180.9 | NO
| NG | 53 | 54 | 74 | 77 | 72.9 | 22.19 | 50 | 68.5 | 12.1 | 42.7 | 17.8 | 223.6 | 180.9 | 180.9 | NO
| NG | 54 | 4 | 74 | 77 | 72.9 | 20.22 | 50 | 68.5 | 12.1 | 45 | 17.8 | 223.3 | 180.9 | 180.9 | NO
| NG | 4 | 44 | 74 | 77 | 72.9 | 19.68 | 50 | 68.5 | 12.1 | 45.6 | 17.4 | 223.3 | 185 | 185 | NO
| NG | 44 | 45 | 74 | 77 | 72.9 | 18.17 | 50 | 68.5 | 12.1 | 47.3 | 17.4 | 223.1 | 185 | 185 | NO
| NG | 45 | 46 | 74 | 77 | 72.9 | 18.17 | 50 | 68.5 | 12.1 | 47.3 | 17.4 | 223.1 | 185 | 185 | NO
| NG | 46 | 40 | 74 | 77 | 72.9 | 18.17 | 50 | 68.5 | 12.1 | 47.3 | 17.4 | 223.1 | 185 | 185 | NO
| NG | 40 | 39 | 74 | 77 | 72.9 | 15.62 | 50 | 68.5 | 12.1 | 50.3 | 16.1 | 223.1 | 198.7 | 198.7 | NO
| NG | 39 | 56 | 74 | 77 | 72.9 | 15.16 | 50 | 68.5 | 12.1 | 50.8 | 16.1 | 223.1 | 198.7 | 198.7 | NO
| NG | 56 | 13 | 74 | 77 | 72.9 | 15.16 | 50 | 68.5 | 12.1 | 50.8 | 16.1 | 223.1 | 198.7 | 198.7 | NO
| NG | 13 | 14 | 74 | 77 | 72.9 | 14.87 | 50 | 68.5 | 12.1 | 51.1 | 16.1 | 223.1 | 198.7 | 198.7 | NO
1 | OK | 14 | 43 | 74 | 77 | 72.9 | 11.49 | 50 | 68.5 | 12.1 | 55.1 | 14.1 | 223.1 | 212.2 | 212.2 | YES
2 | OK | 43 | 75 | 74 | 77 | 72.9 | 11.49 | 50 | 68.5 | 12.1 | 55.1 | 14.1 | 223.1 | 212.2 | 212.2 | YES
3 | ** OPTIMAL ** | 75 | 33 | 74 | 77 | 72.9 | 11.49 | 50 | 68.5 | 12.1 | 55.1 | 14.1 | 223.1 | 212.2 | 212.2 | YES
4 | OK | 33 | 34 | 74 | 77 | 72.9 | 8.79 | 50 | 68.5 | 12.1 | 58.2 | 13.1 | 221.4 | 211.7 | 211.7 | YES
5 | OK | 34 | 15 | 74 | 77 | 72.9 | 5.86 | 50 | 68.5 | 12.1 | 60.7 | 13.1 | 221.8 | 211.7 | 211.7 | YES
6 | OK | 15 | 16 | 74 | 77 | 72.9 | 3.74 | 50 | 68.5 | 12.1 | 64.1 | 12.7 | 220.8 | 211.5 | 211.5 | YES
7 | OK | 16 | 37 | 74 | 77 | 72.9 | 3.18 | 50 | 68.5 | 12.1 | 64.7 | 12.7 | 220.9 | 211.5 | 211.5 | YES
8 | OK | 37 | 38 | 74 | 77 | 72.9 | 1.75 | 50 | 68.5 | 12.1 | 66.4 | 12.7 | 221.1 | 211.5 | 211.5 | YES
9 | OK | 38 | 42 | 74 | 77 | 72.9 | 1.34 | 50 | 68.5 | 12.1 | 66.9 | 12.7 | 221.2 | 211.5 | 211.5 | YES
10 | OK | 42 | 62 | 74 | 77 | 72.9 | 1.34 | 50 | 68.5 | 12.1 | 66.9 | 12.7 | 221.2 | 211.5 | 211.5 | YES
| NG | 62 | 63 | 74 | 77 | 72.9 | 1.34 | 50 | 68.5 | 12.1 | [5 empty] | NO | TR_A sim: loading 3032% (degenerate)
11 | OK | 63 | 59 | 74 | 77 | 72.9 | 1.34 | 50 | 68.5 | 12.1 | 66.9 | 12.7 | 221.2 | 211.5 | 211.5 | YES
12 | OK | 59 | 60 | 64 | 77 | 74.3 | 1.34 | 50 | 68.5 | 12.1 | 66.9 | 12.7 | 221.2 | 211.5 | 211.5 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 65-022494
TR_B (available) | 37-012530
TR_A Rated kVA | 100
TR_B Rated kVA | 250
TR_A Baseline Loading% | 68.5
TR_B Baseline Loading% | 12.1
Total Scenarios Evaluated | 25
Feasible Scenarios | 12
--- Optimal Solution ---
Switch Parent Node | 75
Switch Child Node | 33
Tie Node (TR_A side) | 74
Tie Node (TR_B side) | 77
Tie Line Distance (m) | 72.9
Load Transferred (kW) | 11.49
TR_A Loading After (%) | 55.1
TR_B Loading After (%) | 14.1
Minimum Voltage (V) | 212.2