## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 51 | 36 | 21 | 7 | 11.2 | 34.78 | 50 | 68.5 | 39.8 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 51 | 52 | 40 | 78 | 2.3 | 24.16 | 50 | 68.5 | 39.8 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 36 | 35 | 21 | 7 | 11.2 | 33.33 | 50 | 68.5 | 39.8 | 29.7 | 65 | 220.2 | 211.6 | 211.6 | YES
2 | OK | 52 | 53 | 40 | 78 | 2.3 | 22.51 | 50 | 68.5 | 39.8 | 40.5 | 56.7 | 223.8 | 211.5 | 211.5 | YES
3 | OK | 35 | 6 | 21 | 7 | 11.2 | 33.33 | 50 | 68.5 | 39.8 | 30.1 | 65 | 220.1 | 211.6 | 211.6 | YES
4 | OK | 53 | 54 | 40 | 78 | 2.3 | 22.19 | 50 | 68.5 | 39.8 | 42.7 | 55.5 | 223.6 | 211.3 | 211.3 | YES
5 | OK | 6 | 7 | 21 | 7 | 11.2 | 9.31 | 50 | 68.5 | 39.8 | 57.8 | 46.6 | 218.4 | 217.7 | 217.7 | YES
6 | OK | 6 | 17 | 50 | 71 | 20 | 19.73 | 50 | 68.5 | 39.8 | 45.7 | 44 | 219.1 | 218.2 | 218.2 | YES
7 | OK | 6 | 8 | 2 | 57 | 14.5 | 4.29 | 95 | 68.5 | 39.8 | 63.6 | 43.1 | 217.9 | 218.1 | 217.9 | YES
8 | OK | 54 | 4 | 40 | 78 | 2.3 | 20.22 | 50 | 68.5 | 39.8 | 45 | 55 | 223.3 | 211.2 | 211.2 | YES
9 | OK | 54 | 61 | 61 | 8 | 84.8 | 0.69 | 50 | 68.5 | 39.8 | 67.7 | 40.3 | 217.6 | 218.6 | 217.6 | YES
10 | OK | 7 | 9 | 21 | 7 | 11.2 | 7.55 | 50 | 68.5 | 39.8 | 59.8 | 45.3 | 218.3 | 218.1 | 218.1 | YES
11 | OK | 7 | 10 | 11 | 98 | 67.9 | 1.01 | 50 | 68.5 | 39.8 | 67.4 | 40.2 | 217.8 | 218.6 | 217.8 | YES
12 | OK | 17 | 18 | 50 | 71 | 20 | 18.44 | 50 | 68.5 | 39.8 | 47.1 | 43.1 | 219.1 | 218.4 | 218.4 | YES
13 | OK | 17 | 72 | 72 | 98 | 100.8 | 1.29 | 50 | 68.5 | 39.8 | 67.1 | 40.7 | 217.6 | 218.5 | 217.6 | YES
14 | OK | 8 | 3 | 2 | 57 | 14.5 | 2.32 | 95 | 68.5 | 39.8 | 65.9 | 41.5 | 217.9 | 218.5 | 217.9 | YES
15 | OK | 4 | 5 | 5 | 79 | 50.8 | 0.54 | 50 | 68.5 | 39.8 | 67.9 | 40.1 | 217.9 | 218.5 | 217.9 | YES
16 | OK | 4 | 44 | 40 | 78 | 2.3 | 19.68 | 50 | 68.5 | 39.8 | 45.6 | 54.6 | 223.3 | 211.7 | 211.7 | YES
17 | OK | 9 | 0 | 21 | 7 | 11.2 | 4.82 | 50 | 68.5 | 39.8 | 63 | 43.2 | 217.8 | 218.2 | 217.8 | YES
18 | OK | 10 | 11 | 11 | 98 | 67.9 | 0.58 | 50 | 68.5 | 39.8 | 67.9 | 40.2 | 217.8 | 218.6 | 217.8 | YES
19 | OK | 18 | 68 | 50 | 71 | 20 | 18.3 | 50 | 68.5 | 39.8 | 47.3 | 43.1 | 219.1 | 218.4 | 218.4 | YES
20 | OK | 72 | 73 | 73 | 98 | 102.9 | 1.29 | 50 | 68.5 | 39.8 | 67.1 | 39.8 | 217.6 | 218.6 | 217.6 | YES
21 | OK | 5 | 12 | 12 | 69 | 52.2 | 0.18 | 50 | 68.5 | 39.8 | 68.3 | 39.8 | 217.7 | 218.6 | 217.7 | YES
22 | OK | 44 | 45 | 40 | 78 | 2.3 | 18.17 | 50 | 68.5 | 39.8 | 47.3 | 53.5 | 223.1 | 211.5 | 211.5 | YES
23 | OK | 0 | 1 | 21 | 7 | 11.2 | 4.39 | 50 | 68.5 | 39.8 | 63.5 | 43 | 217.8 | 218.2 | 217.8 | YES
24 | OK | 68 | 20 | 50 | 71 | 20 | 18.3 | 50 | 68.5 | 39.8 | 47.3 | 43.1 | 219.1 | 218.4 | 218.4 | YES
25 | OK | 45 | 46 | 40 | 78 | 2.3 | 18.17 | 50 | 68.5 | 39.8 | 47.3 | 53.5 | 223.1 | 211.5 | 211.5 | YES
26 | OK | 1 | 21 | 21 | 7 | 11.2 | 3.26 | 50 | 68.5 | 39.8 | 64.8 | 42.2 | 217.8 | 218.6 | 217.8 | YES
27 | OK | 20 | 19 | 50 | 71 | 20 | 16.79 | 50 | 68.5 | 39.8 | 49.1 | 42.1 | 219.1 | 218.5 | 218.5 | YES
28 | OK | 46 | 40 | 40 | 78 | 2.3 | 18.17 | 50 | 68.5 | 39.8 | 47.3 | 53.5 | 223.1 | 211.5 | 211.5 | YES
29 | OK | 21 | 22 | 22 | 7 | 18.3 | 3.05 | 50 | 68.5 | 39.8 | 65 | 42 | 217.8 | 218.6 | 217.8 | YES
30 | ** OPTIMAL ** | 19 | 26 | 50 | 71 | 20 | 15.82 | 50 | 68.5 | 39.8 | 50.2 | 41.4 | 219.1 | 218.7 | 218.7 | YES
31 | OK | 40 | 39 | 39 | 102 | 36.5 | 15.62 | 50 | 68.5 | 39.8 | 50.3 | 51.5 | 223.1 | 213.8 | 213.8 | YES
32 | OK | 40 | 25 | 41 | 71 | 3.8 | 2.55 | 50 | 68.5 | 39.8 | 65.6 | 40.2 | 218.8 | 218.6 | 218.6 | YES
33 | OK | 22 | 23 | 23 | 7 | 20.4 | 0.4 | 50 | 68.5 | 39.8 | 68.1 | 39.8 | 217.6 | 218.6 | 217.6 | YES
34 | OK | 26 | 27 | 50 | 71 | 20 | 8.3 | 50 | 68.5 | 39.8 | 58.9 | 40.5 | 218.2 | 218.6 | 218.2 | YES
35 | OK | 26 | 28 | 32 | 55 | 27.5 | 6.64 | 50 | 68.5 | 39.8 | 60.8 | 40.5 | 218.4 | 217.5 | 217.5 | YES
36 | OK | 26 | 29 | 29 | 55 | 75 | 0.47 | 50 | 68.5 | 39.8 | 66.9 | 40 | 217.8 | 218.4 | 217.8 | YES
37 | OK | 39 | 56 | 56 | 102 | 40.2 | 15.16 | 50 | 68.5 | 39.8 | 50.8 | 51.2 | 223.1 | 213.7 | 213.7 | YES
38 | OK | 25 | 24 | 41 | 71 | 3.8 | 2.03 | 50 | 68.5 | 39.8 | 66.2 | 40.2 | 218.5 | 218.6 | 218.5 | YES
39 | OK | 27 | 71 | 50 | 71 | 20 | 8.3 | 50 | 68.5 | 39.8 | 58.9 | 40.5 | 218.2 | 218.6 | 218.2 | YES
40 | OK | 28 | 30 | 32 | 55 | 27.5 | 4.48 | 50 | 68.5 | 39.8 | 63.3 | 40.5 | 218.1 | 217.5 | 217.5 | YES
41 | OK | 28 | 57 | 57 | 55 | 77.5 | 1.61 | 50 | 68.5 | 39.8 | 66.7 | 41.1 | 218 | 216.1 | 216.1 | YES
42 | OK | 56 | 13 | 13 | 102 | 43.1 | 15.16 | 50 | 68.5 | 39.8 | 50.8 | 51 | 223.1 | 213.7 | 213.7 | YES
43 | OK | 71 | 69 | 50 | 71 | 20 | 8.3 | 50 | 68.5 | 39.8 | 58.9 | 40.1 | 218.2 | 218.6 | 218.2 | YES
44 | OK | 30 | 31 | 32 | 55 | 27.5 | 2.36 | 50 | 68.5 | 39.8 | 65.8 | 40.5 | 217.9 | 217.5 | 217.5 | YES
45 | OK | 13 | 14 | 14 | 105 | 72.5 | 14.87 | 50 | 68.5 | 39.8 | 51.1 | 50.9 | 223.1 | 214.2 | 214.2 | YES
46 | OK | 69 | 70 | 50 | 71 | 20 | 7.35 | 50 | 68.5 | 39.8 | 60 | 40.1 | 218.2 | 218.6 | 218.2 | YES
47 | OK | 31 | 32 | 32 | 55 | 27.5 | 2.36 | 50 | 68.5 | 39.8 | 65.8 | 40.5 | 217.9 | 217.5 | 217.5 | YES
| NG | 14 | 43 | 74 | 77 | 75.2 | 11.49 | 50 | 68.5 | 39.8 | 55.1 | 49.7 | 223.1 | 187.2 | 187.2 | NO
48 | OK | 70 | 65 | 50 | 71 | 20 | 6.73 | 50 | 68.5 | 39.8 | 60.7 | 40 | 218.1 | 218.6 | 218.1 | YES
| NG | 43 | 75 | 74 | 77 | 75.2 | 11.49 | 50 | 68.5 | 39.8 | 55.1 | 49.7 | 223.1 | 187.2 | 187.2 | NO
49 | OK | 65 | 66 | 50 | 71 | 20 | 6.34 | 50 | 68.5 | 39.8 | 61.1 | 40 | 218.1 | 218.6 | 218.1 | YES
| NG | 75 | 33 | 74 | 77 | 75.2 | 11.49 | 50 | 68.5 | 39.8 | 55.1 | 49.7 | 223.1 | 187.2 | 187.2 | NO
50 | OK | 66 | 55 | 50 | 71 | 20 | 4.39 | 50 | 68.5 | 39.8 | 63.4 | 40 | 218.1 | 218.6 | 218.1 | YES
| NG | 33 | 34 | 74 | 77 | 75.2 | 8.79 | 50 | 68.5 | 39.8 | 58.2 | 47 | 221.4 | 199.1 | 199.1 | NO
51 | OK | 55 | 47 | 50 | 71 | 20 | 4.39 | 50 | 68.5 | 39.8 | 63.4 | 40 | 218.1 | 218.6 | 218.1 | YES
| NG | 34 | 15 | 74 | 77 | 75.2 | 5.86 | 50 | 68.5 | 39.8 | 60.7 | 44.3 | 221.8 | 209.9 | 209.9 | NO
52 | OK | 47 | 48 | 50 | 71 | 20 | 3.16 | 50 | 68.5 | 39.8 | 64.8 | 40 | 218.1 | 218.6 | 218.1 | YES
53 | OK | 15 | 16 | 74 | 77 | 75.2 | 3.74 | 50 | 68.5 | 39.8 | 64.1 | 42.6 | 220.8 | 217.1 | 217.1 | YES
54 | OK | 48 | 67 | 50 | 71 | 20 | 2.68 | 50 | 68.5 | 39.8 | 65.4 | 39.8 | 218.1 | 218.6 | 218.1 | YES
55 | OK | 16 | 37 | 74 | 77 | 75.2 | 3.18 | 50 | 68.5 | 39.8 | 64.7 | 42.2 | 220.9 | 218.5 | 218.5 | YES
56 | OK | 67 | 49 | 50 | 71 | 20 | 1.9 | 50 | 68.5 | 39.8 | 66.3 | 39.8 | 218.1 | 218.6 | 218.1 | YES
57 | OK | 37 | 38 | 74 | 77 | 75.2 | 1.75 | 50 | 68.5 | 39.8 | 66.4 | 40.9 | 221.1 | 218.7 | 218.7 | YES
58 | OK | 38 | 42 | 74 | 77 | 75.2 | 1.34 | 50 | 68.5 | 39.8 | 66.9 | 40.8 | 221.2 | 218.7 | 218.7 | YES
59 | OK | 42 | 62 | 74 | 77 | 75.2 | 1.34 | 50 | 68.5 | 39.8 | 66.9 | 40.8 | 221.2 | 218.7 | 218.7 | YES
| NG | 62 | 63 | 74 | 77 | 75.2 | 1.34 | 50 | 68.5 | 39.8 | [5 empty] | NO | TR_A sim: loading 1066% (degenerate)
60 | OK | 63 | 59 | 74 | 77 | 75.2 | 1.34 | 50 | 68.5 | 39.8 | 66.9 | 40.8 | 221.2 | 218.7 | 218.7 | YES
61 | OK | 59 | 60 | 64 | 77 | 76.6 | 1.34 | 50 | 68.5 | 39.8 | 66.9 | 40.8 | 221.2 | 218.7 | 218.7 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 65-022494
TR_B (available) | 60-011402
TR_A Rated kVA | 100
TR_B Rated kVA | 160
TR_A Baseline Loading% | 68.5
TR_B Baseline Loading% | 39.8
Total Scenarios Evaluated | 69
Feasible Scenarios | 61
--- Optimal Solution ---
Switch Parent Node | 19
Switch Child Node | 26
Tie Node (TR_A side) | 50
Tie Node (TR_B side) | 71
Tie Line Distance (m) | 20
Load Transferred (kW) | 15.82
TR_A Loading After (%) | 50.2
TR_B Loading After (%) | 41.4
Minimum Voltage (V) | 218.7