## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 8 | 20 | 7 | 61 | 13.7 | 17.54 | 50 | 71.6 | 38.1 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 20 | 19 | 7 | 61 | 13.7 | 17.54 | 50 | 71.6 | 38.1 | 31.2 | 51.6 | 220.9 | 207.3 | 207.3 | NO
1 | OK | 19 | 16 | 7 | 61 | 13.7 | 10.51 | 50 | 71.6 | 38.1 | 47.3 | 46.1 | 220 | 210.8 | 210.8 | YES
2 | OK | 16 | 15 | 7 | 61 | 13.7 | 10.51 | 50 | 71.6 | 38.1 | 47.3 | 46.1 | 220 | 210.8 | 210.8 | YES
3 | OK | 15 | 30 | 7 | 61 | 13.7 | 9.35 | 50 | 71.6 | 38.1 | 50 | 45.1 | 219.4 | 213.7 | 213.7 | YES
4 | OK | 30 | 2 | 7 | 61 | 13.7 | 9.35 | 50 | 71.6 | 38.1 | 50 | 45.1 | 219.4 | 213.7 | 213.7 | YES
5 | OK | 2 | 3 | 7 | 61 | 13.7 | 9.01 | 50 | 71.6 | 38.1 | 50.7 | 44.9 | 219.3 | 214.4 | 214.4 | YES
6 | OK | 3 | 0 | 7 | 61 | 13.7 | 9.01 | 50 | 71.6 | 38.1 | 50.7 | 44.9 | 219.3 | 214.4 | 214.4 | YES
7 | OK | 0 | 1 | 7 | 61 | 13.7 | 3.82 | 50 | 71.6 | 38.1 | 62.7 | 40.9 | 217.2 | 219.7 | 217.2 | YES
8 | ** OPTIMAL ** | 1 | 31 | 7 | 61 | 13.7 | 3.82 | 50 | 71.6 | 38.1 | 62.7 | 40.9 | 217.2 | 219.7 | 217.2 | YES
9 | OK | 31 | 6 | 7 | 61 | 13.7 | 2.99 | 50 | 71.6 | 38.1 | 64.6 | 40.2 | 217.1 | 220.3 | 217.1 | YES
10 | OK | 6 | 4 | 7 | 61 | 13.7 | 2.29 | 50 | 71.6 | 38.1 | 66.3 | 38.9 | 217 | 219.9 | 217 | YES
11 | OK | 4 | 5 | 5 | 64 | 96 | 1.16 | 50 | 71.6 | 38.1 | 68.9 | 38.9 | 217 | 219.9 | 217 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 65-025204
TR_B (available) | 44-000255
TR_A Rated kVA | 50
TR_B Rated kVA | 160
TR_A Baseline Loading% | 71.6
TR_B Baseline Loading% | 38.1
Total Scenarios Evaluated | 13
Feasible Scenarios | 11
--- Optimal Solution ---
Switch Parent Node | 1
Switch Child Node | 31
Tie Node (TR_A side) | 7
Tie Node (TR_B side) | 61
Tie Line Distance (m) | 13.7
Load Transferred (kW) | 3.82
TR_A Loading After (%) | 62.7
TR_B Loading After (%) | 40.9
Minimum Voltage (V) | 217.2