## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 8 | 9 | 9 | 26 | 76.7 | 13.49 | 50 | 71.6 | 46.6 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 8 | 20 | 30 | 26 | 8.9 | 17.54 | 50 | 71.6 | 46.6 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 9 | 12 | 12 | 26 | 81 | 11.66 | 50 | 71.6 | 46.6 | 44.6 | 60.7 | 222 | 210.6 | 210.6 | YES
2 | OK | 20 | 19 | 30 | 26 | 8.9 | 17.54 | 50 | 71.6 | 46.6 | 31.2 | 67.6 | 220.9 | 212.7 | 212.7 | YES
3 | OK | 12 | 10 | 10 | 26 | 83.7 | 11.66 | 50 | 71.6 | 46.6 | 44.6 | 60.7 | 222 | 210.6 | 210.6 | YES
4 | OK | 19 | 25 | 25 | 26 | 25.1 | 5.73 | 50 | 71.6 | 46.6 | 58.4 | 53.3 | 217.3 | 218.6 | 217.3 | YES
5 | OK | 19 | 16 | 30 | 26 | 8.9 | 10.51 | 50 | 71.6 | 46.6 | 47.3 | 59.1 | 220 | 214.6 | 214.6 | YES
6 | OK | 10 | 11 | 11 | 26 | 96.7 | 7 | 50 | 71.6 | 46.6 | 55.5 | 54.9 | 217.7 | 217.3 | 217.3 | YES
7 | OK | 10 | 41 | 41 | 26 | 99 | 4.66 | 50 | 71.6 | 46.6 | 60.6 | 52.2 | 220.9 | 214.1 | 214.1 | YES
8 | OK | 25 | 13 | 13 | 26 | 31.5 | 5.73 | 50 | 71.6 | 46.6 | 58.4 | 52.7 | 217.3 | 218.6 | 217.3 | YES
9 | OK | 16 | 15 | 30 | 26 | 8.9 | 10.51 | 50 | 71.6 | 46.6 | 47.3 | 59.1 | 220 | 214.6 | 214.6 | YES
10 | OK | 13 | 14 | 14 | 26 | 55.9 | 5.23 | 50 | 71.6 | 46.6 | 59.6 | 52.7 | 217.3 | 218.6 | 217.3 | YES
11 | OK | 15 | 30 | 30 | 26 | 8.9 | 9.35 | 50 | 71.6 | 46.6 | 50 | 57.7 | 219.4 | 216.6 | 216.6 | YES
12 | OK | 14 | 27 | 27 | 26 | 63 | 5.23 | 50 | 71.6 | 46.6 | 59.6 | 52.7 | 217.3 | 218.6 | 217.3 | YES
13 | OK | 30 | 2 | 2 | 26 | 21.1 | 9.35 | 50 | 71.6 | 46.6 | 50 | 57.7 | 219.4 | 216.7 | 216.7 | YES
14 | OK | 27 | 28 | 28 | 26 | 65.5 | 2.4 | 50 | 71.6 | 46.6 | 66.1 | 49.4 | 216.4 | 219 | 216.4 | YES
15 | OK | 27 | 21 | 21 | 26 | 83.3 | 2.83 | 50 | 71.6 | 46.6 | 65.1 | 49.9 | 217.3 | 218.6 | 217.3 | YES
16 | ** OPTIMAL ** | 2 | 3 | 6 | 21 | 32.5 | 9.01 | 50 | 71.6 | 46.6 | 50.7 | 57.1 | 219.3 | 217.7 | 217.7 | YES
17 | OK | 21 | 22 | 22 | 26 | 91 | 2.67 | 50 | 71.6 | 46.6 | 65.4 | 49.1 | 217.3 | 218.6 | 217.3 | YES
18 | OK | 3 | 0 | 6 | 21 | 32.5 | 9.01 | 50 | 71.6 | 46.6 | 50.7 | 57.1 | 219.3 | 217.7 | 217.7 | YES
19 | OK | 22 | 23 | 23 | 26 | 93.4 | 0.04 | 50 | 71.6 | 46.6 | 70.6 | 46.6 | 216.6 | 219 | 216.6 | YES
20 | OK | 0 | 1 | 6 | 21 | 32.5 | 3.82 | 50 | 71.6 | 46.6 | 62.7 | 51 | 217.2 | 218.6 | 217.2 | YES
21 | OK | 1 | 31 | 6 | 21 | 32.5 | 3.82 | 50 | 71.6 | 46.6 | 62.7 | 51 | 217.2 | 218.6 | 217.2 | YES
22 | OK | 31 | 6 | 6 | 21 | 32.5 | 2.99 | 50 | 71.6 | 46.6 | 64.6 | 50 | 217.1 | 218.7 | 217.1 | YES
23 | OK | 6 | 4 | 4 | 21 | 35.8 | 2.29 | 95 | 71.6 | 46.6 | 66.3 | 47.9 | 217 | 218.7 | 217 | YES
24 | OK | 4 | 5 | 5 | 21 | 76.8 | 1.16 | 50 | 71.6 | 46.6 | 68.9 | 47.9 | 217 | 218.7 | 217 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 65-025204
TR_B (available) | 54-018072
TR_A Rated kVA | 50
TR_B Rated kVA | 100
TR_A Baseline Loading% | 71.6
TR_B Baseline Loading% | 46.6
Total Scenarios Evaluated | 26
Feasible Scenarios | 24
--- Optimal Solution ---
Switch Parent Node | 2
Switch Child Node | 3
Tie Node (TR_A side) | 6
Tie Node (TR_B side) | 21
Tie Line Distance (m) | 32.5
Load Transferred (kW) | 9.01
TR_A Loading After (%) | 50.7
TR_B Loading After (%) | 57.1
Minimum Voltage (V) | 217.7