## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 8 | 9 | 34 | 72 | 146 | 13.49 | 50 | 71.6 | 43.5 | 40.4 | 51.7 | 222.9 | 183 | 183 | NO
1 | OK | 8 | 20 | 7 | 4 | 18 | 17.54 | 50 | 71.6 | 43.5 | 31.2 | 56.3 | 220.9 | 211.7 | 211.7 | YES
| NG | 9 | 12 | 34 | 72 | 146 | 11.66 | 50 | 71.6 | 43.5 | 44.6 | 49.7 | 222 | 191.2 | 191.2 | NO
2 | OK | 20 | 19 | 7 | 4 | 18 | 17.54 | 50 | 71.6 | 43.5 | 31.2 | 56.3 | 220.9 | 211.7 | 211.7 | YES
| NG | 12 | 10 | 34 | 72 | 146 | 11.66 | 50 | 71.6 | 43.5 | 44.6 | 49.7 | 222 | 191.2 | 191.2 | NO
3 | OK | 19 | 25 | 18 | 72 | 111.7 | 5.73 | 50 | 71.6 | 43.5 | 58.4 | 45 | 217.3 | 210.9 | 210.9 | YES
4 | OK | 19 | 16 | 7 | 4 | 18 | 10.51 | 50 | 71.6 | 43.5 | 47.3 | 51.2 | 220 | 212.1 | 212.1 | YES
| NG | 10 | 41 | 34 | 72 | 146 | 4.66 | 50 | 71.6 | 43.5 | 60.6 | 47.5 | 220.9 | 199.3 | 199.3 | NO
5 | OK | 25 | 13 | 18 | 72 | 111.7 | 5.73 | 50 | 71.6 | 43.5 | 58.4 | 44.6 | 217.3 | 211.2 | 211.2 | YES
6 | OK | 16 | 15 | 7 | 4 | 18 | 10.51 | 50 | 71.6 | 43.5 | 47.3 | 51.2 | 220 | 212.1 | 212.1 | YES
| NG | 41 | 32 | 34 | 72 | 146 | 4.66 | 50 | 71.6 | 43.5 | 60.6 | 47.5 | 220.9 | 199.3 | 199.3 | NO
7 | OK | 13 | 14 | 18 | 72 | 111.7 | 5.23 | 50 | 71.6 | 43.5 | 59.6 | 44.6 | 217.3 | 211.2 | 211.2 | YES
8 | OK | 15 | 30 | 7 | 4 | 18 | 9.35 | 50 | 71.6 | 43.5 | 50 | 50.3 | 219.4 | 212.1 | 212.1 | YES
| NG | 32 | 33 | 34 | 72 | 146 | 4.66 | 50 | 71.6 | 43.5 | 60.6 | 47.5 | 220.9 | 199.3 | 199.3 | NO
9 | OK | 14 | 27 | 18 | 72 | 111.7 | 5.23 | 50 | 71.6 | 43.5 | 59.6 | 44.6 | 217.3 | 211.2 | 211.2 | YES
10 | OK | 30 | 2 | 7 | 4 | 18 | 9.35 | 50 | 71.6 | 43.5 | 50 | 50.3 | 219.4 | 212.1 | 212.1 | YES
| NG | 33 | 34 | 34 | 72 | 146 | 4.41 | 50 | 71.6 | 43.5 | 61.2 | 47.3 | 220.8 | 200.1 | 200.1 | NO
11 | OK | 27 | 28 | 28 | 72 | 155.8 | 2.4 | 50 | 71.6 | 43.5 | 66.1 | 45.4 | 216.4 | 211.9 | 211.9 | YES
12 | OK | 27 | 21 | 18 | 72 | 111.7 | 2.83 | 50 | 71.6 | 43.5 | 65.1 | 44 | 217.3 | 211.7 | 211.7 | YES
13 | OK | 2 | 3 | 7 | 4 | 18 | 9.01 | 50 | 71.6 | 43.5 | 50.7 | 50 | 219.3 | 212.1 | 212.1 | YES
| NG | 34 | 35 | 35 | 72 | 146.7 | 3.16 | 50 | 71.6 | 43.5 | 64.1 | 46.2 | 220.2 | 204.4 | 204.4 | NO
14 | OK | 21 | 22 | 18 | 72 | 111.7 | 2.67 | 50 | 71.6 | 43.5 | 65.4 | 43.5 | 217.3 | 212.1 | 212.1 | YES
15 | OK | 3 | 0 | 7 | 4 | 18 | 9.01 | 50 | 71.6 | 43.5 | 50.7 | 50 | 219.3 | 212.1 | 212.1 | YES
| NG | 35 | 36 | 36 | 72 | 154.6 | 2.3 | 50 | 71.6 | 43.5 | 66.1 | 45.4 | 219.8 | 207.2 | 207.2 | NO
16 | OK | 22 | 23 | 18 | 72 | 111.7 | 0.04 | 50 | 71.6 | 43.5 | 70.6 | 43.5 | 216.6 | 212.1 | 212.1 | YES
17 | OK | 0 | 1 | 7 | 4 | 18 | 3.82 | 50 | 71.6 | 43.5 | 62.7 | 46.2 | 217.2 | 212.1 | 212.1 | YES
| NG | 36 | 37 | 37 | 72 | 166.7 | 1.44 | 50 | 71.6 | 43.5 | 68.1 | 44.7 | 219.3 | 209.7 | 209.7 | NO
18 | OK | 1 | 31 | 7 | 4 | 18 | 3.82 | 50 | 71.6 | 43.5 | 62.7 | 46.2 | 217.2 | 212.1 | 212.1 | YES
19 | ** OPTIMAL ** | 31 | 6 | 7 | 4 | 18 | 2.99 | 50 | 71.6 | 43.5 | 64.6 | 45.6 | 217.1 | 212.1 | 212.1 | YES
20 | OK | 6 | 4 | 7 | 4 | 18 | 2.29 | 50 | 71.6 | 43.5 | 66.3 | 44.3 | 217 | 212.1 | 212.1 | YES
21 | OK | 4 | 5 | 5 | 91 | 85.1 | 1.16 | 50 | 71.6 | 43.5 | 68.9 | 44.3 | 217 | 212.1 | 212.1 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 65-025204
TR_B (available) | 59-018645
TR_A Rated kVA | 50
TR_B Rated kVA | 160
TR_A Baseline Loading% | 71.6
TR_B Baseline Loading% | 43.5
Total Scenarios Evaluated | 31
Feasible Scenarios | 21
--- Optimal Solution ---
Switch Parent Node | 31
Switch Child Node | 6
Tie Node (TR_A side) | 7
Tie Node (TR_B side) | 4
Tie Line Distance (m) | 18
Load Transferred (kW) | 2.99
TR_A Loading After (%) | 64.6
TR_B Loading After (%) | 45.6
Minimum Voltage (V) | 212.1