## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 25 | 24 | 41 | 12 | 4.6 | 4.47 | 50 | 83.1 | 6.9 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 25 | 28 | 3 | 14 | 2.3 | 16.87 | 50 | 83.1 | 6.9 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 24 | 47 | 41 | 12 | 4.6 | 4.05 | 50 | 83.1 | 6.9 | 67.6 | 22.9 | 214.6 | 219.7 | 214.6 | YES
2 | OK | 28 | 3 | 3 | 14 | 2.3 | 16.83 | 50 | 83.1 | 6.9 | 17.3 | 31 | 225.6 | 215.8 | 215.8 | YES
3 | OK | 47 | 42 | 41 | 12 | 4.6 | 3.44 | 50 | 83.1 | 6.9 | 69.9 | 20.4 | 214.6 | 221.1 | 214.6 | YES
4 | OK | 3 | 2 | 2 | 14 | 29.2 | 13.86 | 50 | 83.1 | 6.9 | 28.7 | 23.4 | 224.2 | 219.7 | 219.7 | YES
5 | OK | 3 | 11 | 11 | 14 | 7.2 | 2.97 | 50 | 83.1 | 6.9 | 71.6 | 14.1 | 215.6 | 226.5 | 215.6 | YES
6 | OK | 42 | 41 | 41 | 12 | 4.6 | 3.44 | 50 | 83.1 | 6.9 | 69.9 | 20.4 | 214.6 | 221.1 | 214.6 | YES
7 | OK | 2 | 4 | 4 | 14 | 87.7 | 12.5 | 50 | 83.1 | 6.9 | 33.9 | 20.2 | 223.7 | 221.4 | 221.4 | YES
8 | OK | 11 | 26 | 26 | 14 | 21.9 | 2.97 | 50 | 83.1 | 6.9 | 71.6 | 14.1 | 215.6 | 226.5 | 215.6 | YES
9 | OK | 41 | 29 | 29 | 12 | 20.9 | 3.44 | 50 | 83.1 | 6.9 | 69.9 | 20.4 | 214.6 | 221.1 | 214.6 | YES
10 | OK | 4 | 17 | 17 | 14 | 106.6 | 12.34 | 50 | 83.1 | 6.9 | 34.5 | 19.6 | 223.5 | 221.8 | 221.8 | YES
11 | OK | 26 | 27 | 27 | 14 | 33 | 2.44 | 50 | 83.1 | 6.9 | 73.7 | 12.1 | 215.7 | 227.6 | 215.7 | YES
12 | OK | 29 | 30 | 31 | 12 | 60.8 | 3.42 | 50 | 83.1 | 6.9 | 70 | 20.4 | 214.6 | 220.7 | 214.6 | YES
13 | ** OPTIMAL ** | 17 | 19 | 19 | 14 | 126.8 | 11.5 | 50 | 83.1 | 6.9 | 37.7 | 19.6 | 223.5 | 221.8 | 221.8 | YES
14 | OK | 27 | 16 | 16 | 14 | 58.7 | 2.36 | 50 | 83.1 | 6.9 | 74 | 11.7 | 215.7 | 227.7 | 215.7 | YES
15 | OK | 30 | 32 | 32 | 12 | 108.4 | 2.88 | 50 | 83.1 | 6.9 | 72 | 18.2 | 214.6 | 222.5 | 214.6 | YES
16 | OK | 16 | 0 | 13 | 14 | 62.4 | 2.22 | 50 | 83.1 | 6.9 | 74.5 | 15.5 | 215.5 | 225.1 | 215.5 | YES
17 | OK | 32 | 37 | 35 | 14 | 116.8 | 2.8 | 50 | 83.1 | 6.9 | 72.3 | 17.8 | 214.6 | 223.4 | 214.6 | YES
18 | OK | 0 | 1 | 13 | 14 | 62.4 | 2.22 | 50 | 83.1 | 6.9 | 74.5 | 15.5 | 215.5 | 225.1 | 215.5 | YES
19 | OK | 37 | 38 | 35 | 14 | 116.8 | 2.39 | 50 | 83.1 | 6.9 | 73.9 | 16.2 | 214.6 | 224.5 | 214.6 | YES
20 | OK | 1 | 6 | 13 | 14 | 62.4 | 2.22 | 50 | 83.1 | 6.9 | 74.5 | 10.4 | 215.5 | 228.5 | 215.5 | YES
21 | OK | 38 | 39 | 35 | 14 | 116.8 | 1.45 | 50 | 83.1 | 6.9 | 77.5 | 12.5 | 214.6 | 226.9 | 214.6 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 65-028168
TR_B (available) | 55-001388
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 83.1
TR_B Baseline Loading% | 6.9
Total Scenarios Evaluated | 23
Feasible Scenarios | 21
--- Optimal Solution ---
Switch Parent Node | 17
Switch Child Node | 19
Tie Node (TR_A side) | 19
Tie Node (TR_B side) | 14
Tie Line Distance (m) | 126.8
Load Transferred (kW) | 11.5
TR_A Loading After (%) | 37.7
TR_B Loading After (%) | 19.6
Minimum Voltage (V) | 221.8