## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 33 | 36 | 7 | 23 | 1.9 | 33.69 | 50 | 86.4 | 24.3 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 36 | 15 | 7 | 23 | 1.9 | 33.55 | 50 | 86.4 | 24.3 | 6.1 | 41.1 | 226.1 | 200.9 | 200.9 | NO
| NG | 15 | 14 | 7 | 23 | 1.9 | 32.38 | 50 | 86.4 | 24.3 | 8.8 | 41.1 | 226.1 | 200.9 | 200.9 | NO
| NG | 14 | 7 | 7 | 23 | 1.9 | 32.07 | 50 | 86.4 | 24.3 | 9.5 | 40.7 | 226 | 201.4 | 201.4 | NO
1 | OK | 7 | 0 | 6 | 24 | 2.4 | 18.8 | 50 | 86.4 | 24.3 | 41.8 | 29.3 | 210.1 | 218.9 | 210.1 | YES
| NG | 7 | 16 | 28 | 25 | 2.3 | 13.27 | 50 | 86.4 | 24.3 | 53.4 | 35.2 | 220.7 | 207.4 | 207.4 | NO
| NG | 0 | 1 | 6 | 24 | 2.4 | 10.38 | 50 | 86.4 | 24.3 | 62 | 29.3 | 203.5 | 218.9 | 203.5 | NO
| NG | 16 | 17 | 28 | 25 | 2.3 | 13.27 | 50 | 86.4 | 24.3 | 53.4 | 35.2 | 220.7 | 207.4 | 207.4 | NO
| NG | 1 | 2 | 6 | 24 | 2.4 | 8.25 | 50 | 86.4 | 24.3 | 66.7 | 29.2 | 203.7 | 219.1 | 203.7 | NO
| NG | 17 | 18 | 28 | 25 | 2.3 | 13.27 | 50 | 86.4 | 24.3 | 53.4 | 35.2 | 220.7 | 207.4 | 207.4 | NO
| NG | 2 | 3 | 6 | 24 | 2.4 | 8.25 | 50 | 86.4 | 24.3 | 66.9 | 29.2 | 203.7 | 219.1 | 203.7 | NO
| NG | 18 | 11 | 28 | 25 | 2.3 | 13.12 | 50 | 86.4 | 24.3 | 53.7 | 35 | 220.7 | 207.7 | 207.7 | NO
| NG | 3 | 4 | 6 | 24 | 2.4 | 5.83 | 50 | 86.4 | 24.3 | 72.4 | 29 | 204.1 | 219.3 | 204.1 | NO
| NG | 11 | 12 | 28 | 25 | 2.3 | 13.12 | 50 | 86.4 | 24.3 | 53.7 | 35 | 220.7 | 207.7 | 207.7 | NO
| NG | 4 | 5 | 6 | 24 | 2.4 | 3.51 | 50 | 86.4 | 24.3 | 78 | 26.2 | 204.2 | 224.1 | 204.2 | NO
| NG | 12 | 13 | 28 | 25 | 2.3 | 13.12 | 50 | 86.4 | 24.3 | 53.7 | 35 | 220.7 | 207.7 | 207.7 | NO
| NG | 13 | 26 | 28 | 25 | 2.3 | 13.1 | 50 | 86.4 | 24.3 | 53.8 | 35 | 220.7 | 207.7 | 207.7 | NO
| NG | 26 | 27 | 28 | 25 | 2.3 | 13.1 | 50 | 86.4 | 24.3 | 53.8 | 35 | 220.7 | 207.7 | 207.7 | NO
2 | OK | 27 | 28 | 28 | 25 | 2.3 | 11.87 | 50 | 86.4 | 24.3 | 56.6 | 33.4 | 220.8 | 210.3 | 210.3 | YES
3 | OK | 28 | 29 | 29 | 25 | 9.1 | 11.87 | 50 | 86.4 | 24.3 | 56.6 | 33.4 | 220.8 | 210.4 | 210.4 | YES
4 | OK | 29 | 30 | 30 | 25 | 32.2 | 11.87 | 50 | 86.4 | 24.3 | 56.6 | 33.4 | 220.8 | 210.4 | 210.4 | YES
5 | OK | 30 | 32 | 32 | 25 | 38 | 11.87 | 50 | 86.4 | 24.3 | 56.6 | 33.4 | 220.8 | 210.3 | 210.3 | YES
6 | OK | 32 | 41 | 41 | 25 | 51.9 | 11.87 | 50 | 86.4 | 24.3 | 56.6 | 33.4 | 220.8 | 210.1 | 210.1 | YES
7 | ** OPTIMAL ** | 41 | 46 | 46 | 25 | 80.6 | 9.42 | 50 | 86.4 | 24.3 | 62.5 | 30.2 | 218.5 | 215.4 | 215.4 | YES
8 | OK | 46 | 50 | 50 | 25 | 130.5 | 9.42 | 50 | 86.4 | 24.3 | 62.5 | 30.3 | 218.5 | 215.1 | 215.1 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 65-031825
TR_B (available) | 52-003041
TR_A Rated kVA | 50
TR_B Rated kVA | 100
TR_A Baseline Loading% | 86.4
TR_B Baseline Loading% | 24.3
Total Scenarios Evaluated | 25
Feasible Scenarios | 8
--- Optimal Solution ---
Switch Parent Node | 41
Switch Child Node | 46
Tie Node (TR_A side) | 46
Tie Node (TR_B side) | 25
Tie Line Distance (m) | 80.6
Load Transferred (kW) | 9.42
TR_A Loading After (%) | 62.5
TR_B Loading After (%) | 30.2
Minimum Voltage (V) | 215.4