## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 7 | 47 | 21 | 15 | 18.3 | 15.68 | 50 | 95.4 | 27.3 | 32.7 | 90.3 | 223.1 | 199.5 | 199.5 | NO
| NG | 47 | 20 | 21 | 15 | 18.3 | 13.03 | 50 | 95.4 | 27.3 | 42.9 | 79.3 | 220.4 | 203.5 | 203.5 | NO
| NG | 20 | 21 | 21 | 15 | 18.3 | 13.03 | 50 | 95.4 | 27.3 | 42.9 | 79.3 | 220.4 | 203.5 | 203.5 | NO
| NG | 21 | 22 | 22 | 15 | 19.6 | 13.03 | 50 | 95.4 | 27.3 | 42.9 | 74.6 | 220.4 | 205.3 | 205.3 | NO
1 | ** OPTIMAL ** | 22 | 23 | 29 | 14 | 20.7 | 7.26 | 50 | 95.4 | 27.3 | 65.7 | 55.2 | 211.9 | 217.4 | 211.9 | YES
2 | OK | 23 | 26 | 29 | 14 | 20.7 | 7.11 | 50 | 95.4 | 27.3 | 66.3 | 54.7 | 211.7 | 217.5 | 211.7 | YES
3 | OK | 26 | 27 | 29 | 14 | 20.7 | 5.88 | 50 | 95.4 | 27.3 | 71.2 | 49.9 | 210.2 | 218.4 | 210.2 | YES
| NG | 27 | 28 | 29 | 14 | 20.7 | 4.88 | 50 | 95.4 | 27.3 | 75.2 | 46.1 | 209 | 219.2 | 209 | NO
| NG | 28 | 29 | 29 | 14 | 20.7 | 4.88 | 50 | 95.4 | 27.3 | 75.2 | 46.1 | 209 | 219.2 | 209 | NO
| NG | 29 | 30 | 30 | 4 | 20.9 | 4.83 | 50 | 95.4 | 27.3 | 75.4 | 45.9 | 208.9 | 219.1 | 208.9 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 66-006968
TR_B (available) | 63-013212
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 95.4
TR_B Baseline Loading% | 27.3
Total Scenarios Evaluated | 10
Feasible Scenarios | 3
--- Optimal Solution ---
Switch Parent Node | 22
Switch Child Node | 23
Tie Node (TR_A side) | 29
Tie Node (TR_B side) | 14
Tie Line Distance (m) | 20.7
Load Transferred (kW) | 7.26
TR_A Loading After (%) | 65.7
TR_B Loading After (%) | 55.2
Minimum Voltage (V) | 211.9