## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 5 | 6 | 6 | 9 | 143.7 | 3 | 50 | 85.4 | 47.3 | 68 | 55.2 | 213.6 | 222.2 | 213.6 | YES
2 | ** OPTIMAL ** | 5 | 7 | 42 | 9 | 1.4 | 9.07 | 50 | 85.4 | 47.3 | 44.2 | 63.7 | 218.9 | 216.8 | 216.8 | YES
| NG | 5 | 37 | 37 | 9 | 147.6 | 3.05 | 50 | 85.4 | 47.3 | 72.9 | 54.3 | 209.8 | 223.3 | 209.8 | NO
3 | OK | 7 | 8 | 42 | 9 | 1.4 | 9.07 | 50 | 85.4 | 47.3 | 48.8 | 63.7 | 216.9 | 216.8 | 216.8 | YES
4 | OK | 8 | 9 | 42 | 9 | 1.4 | 7.58 | 50 | 85.4 | 47.3 | 54.5 | 63.3 | 216.8 | 217.1 | 216.8 | YES
5 | OK | 9 | 29 | 42 | 9 | 1.4 | 6.08 | 50 | 85.4 | 47.3 | 60.6 | 58.3 | 214.7 | 219.4 | 214.7 | YES
6 | OK | 29 | 10 | 10 | 9 | 71.9 | 5 | 50 | 85.4 | 47.3 | 63.2 | 66.7 | 213.3 | 219.7 | 213.3 | YES
7 | OK | 10 | 11 | 11 | 9 | 102.9 | 4.27 | 50 | 85.4 | 47.3 | 68 | 63.8 | 212.1 | 220.8 | 212.1 | YES
8 | OK | 11 | 12 | 12 | 9 | 140.5 | 3.74 | 50 | 85.4 | 47.3 | 70.1 | 61.7 | 211.9 | 221.3 | 211.9 | YES
9 | OK | 12 | 13 | 13 | 9 | 142.8 | 3.74 | 50 | 85.4 | 47.3 | 70.1 | 61.7 | 211.9 | 221.3 | 211.9 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 66-007454
TR_B (available) | 55-015132
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 85.4
TR_B Baseline Loading% | 47.3
Total Scenarios Evaluated | 10
Feasible Scenarios | 9
--- Optimal Solution ---
Switch Parent Node | 5
Switch Child Node | 7
Tie Node (TR_A side) | 42
Tie Node (TR_B side) | 9
Tie Line Distance (m) | 1.4
Load Transferred (kW) | 9.07
TR_A Loading After (%) | 44.2
TR_B Loading After (%) | 63.7
Minimum Voltage (V) | 216.8