## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 25 | 7 | 7 | 56 | 67.9 | 8.21 | 50 | 89.4 | 42.2 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 25 | 8 | 22 | 55 | 5.7 | 14.92 | 50 | 89.4 | 42.2 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 7 | 9 | 9 | 63 | 73.4 | 7.43 | 50 | 89.4 | 42.2 | 60.9 | 51.1 | 218.7 | 215.6 | 215.6 | YES
2 | OK | 8 | 0 | 22 | 55 | 5.7 | 14.92 | 50 | 89.4 | 42.2 | 31.5 | 60.3 | 225.9 | 211.9 | 211.9 | YES
3 | OK | 9 | 23 | 23 | 59 | 74.2 | 7.09 | 50 | 89.4 | 42.2 | 62.2 | 50.7 | 218.4 | 215.6 | 215.6 | YES
4 | OK | 0 | 15 | 22 | 55 | 5.7 | 13.74 | 50 | 89.4 | 42.2 | 36 | 58.9 | 225.3 | 212.9 | 212.9 | YES
5 | OK | 23 | 11 | 11 | 57 | 83.1 | 6.52 | 50 | 89.4 | 42.2 | 64.4 | 50 | 218.4 | 215.8 | 215.8 | YES
6 | OK | 15 | 22 | 22 | 55 | 5.7 | 11.86 | 50 | 89.4 | 42.2 | 43.1 | 56.5 | 224.9 | 212.7 | 212.7 | YES
7 | OK | 11 | 10 | 10 | 57 | 92 | 5.97 | 50 | 89.4 | 42.2 | 66.5 | 49.3 | 218.2 | 215.9 | 215.9 | YES
8 | OK | 22 | 31 | 31 | 57 | 19.7 | 11.86 | 50 | 89.4 | 42.2 | 43.1 | 56.6 | 224.9 | 212.6 | 212.6 | YES
9 | OK | 10 | 12 | 12 | 57 | 104.8 | 4.77 | 50 | 89.4 | 42.2 | 71.1 | 47.9 | 217.3 | 215.9 | 215.9 | YES
10 | OK | 31 | 28 | 28 | 57 | 44.4 | 10.09 | 50 | 89.4 | 42.2 | 49.9 | 54.4 | 224.4 | 214.6 | 214.6 | YES
11 | OK | 12 | 13 | 13 | 57 | 112.3 | 4.34 | 50 | 89.4 | 42.2 | 72.7 | 47.3 | 217.3 | 216 | 216 | YES
12 | OK | 28 | 16 | 16 | 57 | 51.5 | 9.09 | 50 | 89.4 | 42.2 | 50.7 | 53.2 | 224.4 | 214.5 | 214.5 | YES
13 | ** OPTIMAL ** | 13 | 14 | 14 | 57 | 139.6 | 3.3 | 50 | 89.4 | 42.2 | 76.7 | 46.1 | 217.3 | 216.2 | 216.2 | YES
14 | OK | 16 | 17 | 19 | 61 | 85.6 | 6.91 | 50 | 89.4 | 42.2 | 62.2 | 50.5 | 221 | 215.1 | 215.1 | YES
15 | OK | 17 | 18 | 19 | 61 | 85.6 | 6.31 | 50 | 89.4 | 42.2 | 64.6 | 49.8 | 220 | 215 | 215 | YES
16 | OK | 18 | 19 | 19 | 61 | 85.6 | 6.2 | 50 | 89.4 | 42.2 | 65 | 49.7 | 219.8 | 215 | 215 | YES
17 | OK | 19 | 32 | 32 | 61 | 129.5 | 3.2 | 50 | 89.4 | 42.2 | 76.8 | 46.1 | 215 | 215.8 | 215 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 66-007598
TR_B (available) | 61-010127
TR_A Rated kVA | 30
TR_B Rated kVA | 100
TR_A Baseline Loading% | 89.4
TR_B Baseline Loading% | 42.2
Total Scenarios Evaluated | 19
Feasible Scenarios | 17
--- Optimal Solution ---
Switch Parent Node | 13
Switch Child Node | 14
Tie Node (TR_A side) | 14
Tie Node (TR_B side) | 57
Tie Line Distance (m) | 139.6
Load Transferred (kW) | 3.3
TR_A Loading After (%) | 76.7
TR_B Loading After (%) | 46.1
Minimum Voltage (V) | 216.2