## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 1 | 2 | 7 | 40 | 6.6 | 2.78 | 50 | 79.6 | 58.2 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 2 | 6 | 7 | 40 | 6.6 | 0.86 | 50 | 79.6 | 58.2 | 76.3 | 61.6 | 197.6 | 214.8 | 197.6 | NO
| NG | 6 | 7 | 7 | 40 | 6.6 | 0.86 | 50 | 79.6 | 58.2 | 76.3 | 61.6 | 197.6 | 214.8 | 197.6 | NO
| NG | 9 | 28 | 41 | 19 | 5.9 | 6.46 | 50 | 79.6 | 58.2 | 52.5 | 83.8 | 207.8 | 206.7 | 206.7 | NO
| NG | 9 | 13 | 48 | 3 | 90.4 | 2.9 | 50 | 79.6 | 58.2 | 67.3 | 69.9 | 202.3 | 209 | 202.3 | NO
| NG | 7 | 8 | 8 | 40 | 87.3 | 0.86 | 50 | 79.6 | 58.2 | 76.3 | 61.6 | 197.6 | 214.8 | 197.6 | NO
| NG | 28 | 29 | 41 | 19 | 5.9 | 6.09 | 50 | 79.6 | 58.2 | 54 | 82.3 | 207.3 | 207.5 | 207.3 | NO
| NG | 13 | 12 | 48 | 3 | 90.4 | 2.77 | 50 | 79.6 | 58.2 | 67.9 | 69.4 | 202.1 | 209.3 | 202.1 | NO
| NG | 58 | 57 | 52 | 34 | 4.2 | 6.15 | 50 | 79.6 | 58.2 | 53.2 | 82.4 | 212 | 207.2 | 207.2 | NO
| NG | 29 | 30 | 41 | 19 | 5.9 | 5.02 | 50 | 79.6 | 58.2 | 58.3 | 78 | 205.7 | 209.6 | 205.7 | NO
| NG | 12 | 49 | 48 | 3 | 90.4 | 2.14 | 50 | 79.6 | 58.2 | 70.2 | 66.8 | 201.2 | 211 | 201.2 | NO
| NG | 12 | 56 | 56 | 3 | 131.5 | 0.63 | 50 | 79.6 | 58.2 | 76.9 | 60.4 | 198.7 | 214.8 | 198.7 | NO
| NG | 57 | 50 | 52 | 34 | 4.2 | 5.34 | 50 | 79.6 | 58.2 | 56.5 | 79.1 | 210.9 | 209.5 | 209.5 | NO
| NG | 30 | 43 | 41 | 19 | 5.9 | 3.28 | 50 | 79.6 | 58.2 | 65.6 | 71 | 203 | 213 | 203 | NO
| NG | 30 | 54 | 54 | 3 | 49.2 | 1.74 | 50 | 79.6 | 58.2 | 72.1 | 65.2 | 200.5 | 212.3 | 200.5 | NO
| NG | 49 | 47 | 48 | 3 | 90.4 | 1.3 | 50 | 79.6 | 58.2 | 74.1 | 63.4 | 199.8 | 213.1 | 199.8 | NO
| NG | 50 | 51 | 52 | 34 | 4.2 | 5.12 | 50 | 79.6 | 58.2 | 57.4 | 78.2 | 210.5 | 210 | 210 | NO
| NG | 43 | 31 | 41 | 19 | 5.9 | 3.11 | 50 | 79.6 | 58.2 | 66.3 | 70.3 | 202.7 | 213.2 | 202.7 | NO
| NG | 54 | 55 | 55 | 3 | 79.2 | 1.38 | 50 | 79.6 | 58.2 | 73.6 | 63.7 | 199.9 | 213.1 | 199.9 | NO
| NG | 47 | 48 | 48 | 3 | 90.4 | 0.72 | 50 | 79.6 | 58.2 | 76.5 | 61.1 | 198.8 | 214.5 | 198.8 | NO
1 | ** OPTIMAL ** | 51 | 17 | 52 | 34 | 4.2 | 4.92 | 50 | 79.6 | 58.2 | 58.3 | 77.4 | 210.2 | 210.5 | 210.2 | YES
| NG | 31 | 32 | 41 | 19 | 5.9 | 2.74 | 50 | 79.6 | 58.2 | 67.8 | 68.9 | 202.1 | 213.5 | 202.1 | NO
| NG | 48 | 25 | 25 | 3 | 99.2 | 0.22 | 50 | 79.6 | 58.2 | 78.7 | 59.1 | 198 | 215.6 | 198 | NO
| NG | 17 | 16 | 16 | 29 | 95.2 | 0.78 | 50 | 79.6 | 58.2 | 76.1 | 61.3 | 199.8 | 215 | 199.8 | NO
| NG | 17 | 18 | 52 | 34 | 4.2 | 4.14 | 50 | 79.6 | 58.2 | 61.5 | 74.3 | 209.1 | 212.3 | 209.1 | NO
| NG | 32 | 3 | 41 | 19 | 5.9 | 2.54 | 50 | 79.6 | 58.2 | 68.7 | 68.1 | 201.8 | 213.7 | 201.8 | NO
| NG | 16 | 15 | 15 | 29 | 122.8 | 0.78 | 50 | 79.6 | 58.2 | 76.1 | 61.3 | 199.8 | 215 | 199.8 | NO
| NG | 18 | 19 | 52 | 34 | 4.2 | 3.08 | 50 | 79.6 | 58.2 | 66 | 70.1 | 207.4 | 213.6 | 207.4 | NO
| NG | 3 | 4 | 38 | 17 | 25.1 | 0.27 | 50 | 79.6 | 58.2 | 78.4 | 59.2 | 198.1 | 215.9 | 198.1 | NO
| NG | 3 | 5 | 41 | 19 | 5.9 | 1.4 | 50 | 79.6 | 58.2 | 73.5 | 63.6 | 200 | 214.8 | 200 | NO
| NG | 3 | 39 | 39 | 17 | 85.8 | 0.87 | 50 | 79.6 | 58.2 | 75.8 | 61.6 | 199.1 | 215.4 | 199.1 | NO
| NG | 19 | 20 | 52 | 34 | 4.2 | 2.79 | 50 | 79.6 | 58.2 | 67.2 | 69 | 207 | 213.9 | 207 | NO
| NG | 5 | 33 | 41 | 19 | 5.9 | 0.69 | 50 | 79.6 | 58.2 | 76.6 | 60.9 | 198.8 | 215.5 | 198.8 | NO
| NG | 39 | 34 | 34 | 17 | 90.2 | 0.87 | 50 | 79.6 | 58.2 | 75.8 | 61.6 | 199.1 | 215.4 | 199.1 | NO
| NG | 20 | 22 | 52 | 34 | 4.2 | 2.79 | 50 | 79.6 | 58.2 | 67.2 | 69 | 207 | 213.9 | 207 | NO
| NG | 33 | 40 | 41 | 19 | 5.9 | 0.18 | 50 | 79.6 | 58.2 | 78.8 | 58.9 | 197.9 | 215.9 | 197.9 | NO
| NG | 34 | 35 | 35 | 3 | 107.5 | 0.19 | 50 | 79.6 | 58.2 | 78.8 | 59 | 197.9 | 215.7 | 197.9 | NO
| NG | 22 | 21 | 52 | 34 | 4.2 | 2.39 | 50 | 79.6 | 58.2 | 68.9 | 67.4 | 205.9 | 214.2 | 205.9 | NO
| NG | 21 | 23 | 52 | 34 | 4.2 | 0.85 | 50 | 79.6 | 58.2 | 75.7 | 61.5 | 200.7 | 215.4 | 200.7 | NO
| NG | 23 | 24 | 52 | 34 | 4.2 | 0.34 | 50 | 79.6 | 58.2 | 78 | 59.5 | 198.9 | 215.8 | 198.9 | NO
| NG | 24 | 53 | 52 | 34 | 4.2 | 0.16 | 50 | 79.6 | 58.2 | 78.9 | 58.8 | 198.2 | 216 | 198.2 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 66-009342
TR_B (available) | 64-007226
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 79.6
TR_B Baseline Loading% | 58.2
Total Scenarios Evaluated | 41
Feasible Scenarios | 1
--- Optimal Solution ---
Switch Parent Node | 51
Switch Child Node | 17
Tie Node (TR_A side) | 52
Tie Node (TR_B side) | 34
Tie Line Distance (m) | 4.2
Load Transferred (kW) | 4.92
TR_A Loading After (%) | 58.3
TR_B Loading After (%) | 77.4
Minimum Voltage (V) | 210.2