## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 23 | 21 | 3 | 10 | 46.9 | 16.9 | 50 | 78.7 | 35.5 | 4.7 | 53.2 | 8.9 | 209.1 | 8.9 | NO
1 | OK | 21 | 20 | 3 | 10 | 46.9 | 16.11 | 50 | 78.7 | 35.5 | 59.1 | 51.1 | 217.8 | 211.4 | 211.4 | YES
2 | OK | 20 | 2 | 3 | 10 | 46.9 | 16.11 | 50 | 78.7 | 35.5 | 59.1 | 51.1 | 217.8 | 211.4 | 211.4 | YES
3 | OK | 2 | 1 | 3 | 10 | 46.9 | 14.88 | 50 | 78.7 | 35.5 | 60.6 | 48.1 | 217.8 | 214.4 | 214.4 | YES
4 | ** OPTIMAL ** | 1 | 8 | 3 | 10 | 46.9 | 7.47 | 50 | 78.7 | 35.5 | 69.5 | 44.3 | 214.7 | 218.3 | 214.7 | YES
5 | OK | 8 | 67 | 3 | 10 | 46.9 | 7.29 | 50 | 78.7 | 35.5 | 69.8 | 44.3 | 214.6 | 218.3 | 214.6 | YES
6 | OK | 67 | 55 | 3 | 10 | 46.9 | 7.29 | 50 | 78.7 | 35.5 | 69.8 | 44.3 | 214.6 | 218.3 | 214.6 | YES
7 | OK | 55 | 56 | 3 | 10 | 46.9 | 5.64 | 50 | 78.7 | 35.5 | 71.8 | 43.4 | 213.8 | 219 | 213.8 | YES
8 | OK | 56 | 6 | 3 | 10 | 46.9 | 4.27 | 50 | 78.7 | 35.5 | 73.4 | 40.3 | 213.9 | 221.6 | 213.9 | YES
9 | OK | 6 | 7 | 3 | 10 | 46.9 | 3.08 | 50 | 78.7 | 35.5 | 74.9 | 37.5 | 214 | 223.7 | 214 | YES
10 | OK | 7 | 52 | 3 | 10 | 46.9 | 2.4 | 50 | 78.7 | 35.5 | 75.7 | 36.7 | 213.8 | 224.3 | 213.8 | YES
11 | OK | 52 | 53 | 53 | 10 | 95.6 | 1.25 | 50 | 78.7 | 35.5 | 76.5 | 36.4 | 213.4 | 224.5 | 213.4 | YES
12 | OK | 52 | 54 | 3 | 10 | 46.9 | 1.15 | 50 | 78.7 | 35.5 | 77.3 | 35.5 | 213.7 | 225.1 | 213.7 | YES
13 | OK | 54 | 4 | 3 | 10 | 46.9 | 1.15 | 50 | 78.7 | 35.5 | 77.3 | 35.5 | 213.7 | 225.1 | 213.7 | YES
14 | OK | 4 | 3 | 3 | 10 | 46.9 | 0.59 | 50 | 78.7 | 35.5 | 77.9 | 35.5 | 213.8 | 225.1 | 213.8 | YES
15 | OK | 4 | 69 | 69 | 10 | 49.9 | 0.56 | 50 | 78.7 | 35.5 | 78 | 35.5 | 213.3 | 225.1 | 213.3 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 66-010914
TR_B (available) | 29-002768
TR_A Rated kVA | 100
TR_B Rated kVA | 50
TR_A Baseline Loading% | 78.7
TR_B Baseline Loading% | 35.5
Total Scenarios Evaluated | 16
Feasible Scenarios | 15
--- Optimal Solution ---
Switch Parent Node | 1
Switch Child Node | 8
Tie Node (TR_A side) | 3
Tie Node (TR_B side) | 10
Tie Line Distance (m) | 46.9
Load Transferred (kW) | 7.47
TR_A Loading After (%) | 69.5
TR_B Loading After (%) | 44.3
Minimum Voltage (V) | 214.7