## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 73 | 72 | 23 | 60 | 3.9 | 50.74 | 50 | 78.7 | 22.9 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 73 | 74 | 74 | 60 | 107.7 | 15.77 | 50 | 78.7 | 22.9 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 72 | 75 | 23 | 60 | 3.9 | 50.11 | 50 | 78.7 | 22.9 | 19.1 | 48.3 | 220.5 | 48.5 | 48.5 | NO
| NG | 74 | 30 | 60 | 60 | 127.4 | 14.99 | 50 | 78.7 | 22.9 | 61.2 | 30.2 | 214.8 | 48.7 | 48.7 | NO
| NG | 75 | 19 | 23 | 60 | 3.9 | 48.85 | 50 | 78.7 | 22.9 | 20.5 | 47.6 | 220.5 | 48.5 | 48.5 | NO
| NG | 30 | 31 | 60 | 60 | 127.4 | 14.99 | 50 | 78.7 | 22.9 | 61.2 | 30.2 | 214.8 | 48.7 | 48.7 | NO
| NG | 19 | 23 | 23 | 60 | 3.9 | 48.85 | 50 | 78.7 | 22.9 | 0 | 47.6 | 7.3 | 48.5 | 7.3 | NO
| NG | 31 | 10 | 60 | 60 | 127.4 | 14.54 | 50 | 78.7 | 22.9 | 61.7 | 30 | 214.8 | 48.7 | 48.7 | NO
| NG | 23 | 22 | 41 | 60 | 21.2 | 31.95 | 50 | 78.7 | 22.9 | 40.3 | 38.8 | 218.7 | 48.5 | 48.5 | NO
| NG | 23 | 21 | 21 | 60 | 6.3 | 16.9 | 50 | 78.7 | 22.9 | 0 | 31 | 6 | 49 | 6 | NO
| NG | 10 | 11 | 60 | 60 | 127.4 | 12.75 | 50 | 78.7 | 22.9 | 63.8 | 29.1 | 214.4 | 48.7 | 48.7 | NO
| NG | 22 | 34 | 41 | 60 | 21.2 | 31.95 | 50 | 78.7 | 22.9 | 40.3 | 38.8 | 218.7 | 48.5 | 48.5 | NO
| NG | 21 | 20 | 20 | 60 | 47.3 | 16.11 | 50 | 78.7 | 22.9 | 59.1 | 30.6 | 217.8 | 49 | 49 | NO
| NG | 11 | 59 | 60 | 60 | 127.4 | 12.03 | 50 | 78.7 | 22.9 | 64.6 | 28.7 | 214.3 | 48.7 | 48.7 | NO
| NG | 34 | 33 | 41 | 60 | 21.2 | 31.28 | 50 | 78.7 | 22.9 | 41.1 | 38.4 | 218.6 | 48.5 | 48.5 | NO
| NG | 20 | 2 | 2 | 60 | 84.2 | 16.11 | 50 | 78.7 | 22.9 | 59.1 | 30.6 | 217.8 | 49 | 49 | NO
| NG | 59 | 12 | 60 | 60 | 127.4 | 12.03 | 50 | 78.7 | 22.9 | 64.6 | 28.7 | 214.3 | 48.7 | 48.7 | NO
| NG | 33 | 36 | 41 | 60 | 21.2 | 30.34 | 50 | 78.7 | 22.9 | 42.2 | 37.8 | 218.6 | 48.5 | 48.5 | NO
| NG | 2 | 1 | 3 | 14 | 116.4 | 14.88 | 50 | 78.7 | 22.9 | 60.6 | 30.7 | 217.8 | 49 | 49 | NO
| NG | 12 | 13 | 60 | 60 | 127.4 | 9.82 | 50 | 78.7 | 22.9 | 67.1 | 27.7 | 214.3 | 48.7 | 48.7 | NO
1 | ** OPTIMAL ** | 36 | 35 | 70 | 41 | 82.2 | 22.85 | 50 | 78.7 | 22.9 | 51 | 26.4 | 218.2 | 214.8 | 214.8 | YES
| NG | 36 | 43 | 41 | 60 | 21.2 | 7.22 | 50 | 78.7 | 22.9 | 69.9 | 26.3 | 214.3 | 48.9 | 48.9 | NO
| NG | 1 | 8 | 3 | 14 | 116.4 | 7.47 | 50 | 78.7 | 22.9 | 69.5 | 26.7 | 214.7 | 49 | 49 | NO
| NG | 13 | 60 | 60 | 60 | 127.4 | 3.03 | 50 | 78.7 | 22.9 | 75.1 | 24.3 | 213.3 | 48.8 | 48.8 | NO
2 | OK | 35 | 28 | 70 | 41 | 82.2 | 22.11 | 50 | 78.7 | 22.9 | 51.8 | 26.1 | 218.2 | 214.8 | 214.8 | YES
| NG | 43 | 39 | 41 | 60 | 21.2 | 7.22 | 50 | 78.7 | 22.9 | 69.9 | 26.3 | 214.3 | 48.9 | 48.9 | NO
| NG | 8 | 67 | 3 | 14 | 116.4 | 7.29 | 50 | 78.7 | 22.9 | 69.8 | 26.6 | 214.6 | 49 | 49 | NO
3 | OK | 28 | 26 | 70 | 41 | 82.2 | 12.46 | 50 | 78.7 | 22.9 | 63.5 | 25.1 | 214.1 | 214.8 | 214.1 | YES
| NG | 39 | 40 | 40 | 60 | 90 | 4.65 | 50 | 78.7 | 22.9 | 73 | 25.1 | 214.1 | 48.9 | 48.9 | NO
| NG | 39 | 42 | 41 | 60 | 21.2 | 2.47 | 50 | 78.7 | 22.9 | 75.7 | 24 | 213.4 | 49 | 49 | NO
| NG | 39 | 50 | 50 | 60 | 114.6 | 0.1 | 50 | 78.7 | 22.9 | 78.6 | 22.9 | 213.3 | 49 | 49 | NO
| NG | 67 | 55 | 3 | 14 | 116.4 | 7.29 | 50 | 78.7 | 22.9 | 69.8 | 26.6 | 214.6 | 49 | 49 | NO
4 | OK | 26 | 45 | 70 | 41 | 82.2 | 10.22 | 50 | 78.7 | 22.9 | 66.2 | 25.1 | 214.8 | 214.8 | 214.8 | YES
| NG | 40 | 24 | 24 | 60 | 116.3 | 4.65 | 50 | 78.7 | 22.9 | 73 | 25.1 | 214.1 | 48.9 | 48.9 | NO
| NG | 42 | 41 | 41 | 60 | 21.2 | 0.83 | 50 | 78.7 | 22.9 | 77.6 | 23.3 | 213.8 | 49 | 49 | NO
| NG | 55 | 56 | 3 | 14 | 116.4 | 5.64 | 50 | 78.7 | 22.9 | 71.8 | 25.7 | 213.8 | 49 | 49 | NO
5 | OK | 45 | 66 | 70 | 41 | 82.2 | 9.01 | 50 | 78.7 | 22.9 | 67.6 | 24.8 | 215 | 214.8 | 214.8 | YES
| NG | 24 | 25 | 25 | 60 | 138.7 | 2.25 | 50 | 78.7 | 22.9 | 75.9 | 23.9 | 214.2 | 49 | 49 | NO
| NG | 56 | 6 | 3 | 14 | 116.4 | 4.27 | 50 | 78.7 | 22.9 | 73.4 | 25 | 213.9 | 49 | 49 | NO
6 | OK | 66 | 58 | 70 | 41 | 82.2 | 8.41 | 50 | 78.7 | 22.9 | 68.4 | 24.8 | 214.2 | 214.8 | 214.2 | YES
| NG | 6 | 7 | 3 | 14 | 116.4 | 3.08 | 50 | 78.7 | 22.9 | 74.9 | 24.4 | 214 | 49 | 49 | NO
7 | OK | 58 | 46 | 70 | 41 | 82.2 | 7.93 | 50 | 78.7 | 22.9 | 68.4 | 24.8 | 214.2 | 214.8 | 214.2 | YES
| NG | 7 | 52 | 3 | 14 | 116.4 | 2.4 | 50 | 78.7 | 22.9 | 75.7 | 24 | 213.8 | 49 | 49 | NO
8 | OK | 46 | 47 | 70 | 41 | 82.2 | 6.37 | 50 | 78.7 | 22.9 | 70.9 | 24.6 | 213.4 | 214.8 | 213.4 | YES
| NG | 52 | 53 | 71 | 16 | 118 | 1.25 | 50 | 78.7 | 22.9 | 76.5 | 23.5 | 213.4 | 49 | 49 | NO
| NG | 52 | 54 | 3 | 14 | 116.4 | 1.15 | 50 | 78.7 | 22.9 | 77.3 | 23.2 | 213.7 | 49 | 49 | NO
9 | OK | 47 | 48 | 70 | 41 | 82.2 | 4.05 | 50 | 78.7 | 22.9 | 73.7 | 24 | 213.8 | 214.8 | 213.8 | YES
| NG | 54 | 4 | 3 | 14 | 116.4 | 1.15 | 50 | 78.7 | 22.9 | 77.3 | 23.2 | 213.7 | 49 | 49 | NO
| NG | 4 | 3 | 3 | 14 | 116.4 | 0.59 | 50 | 78.7 | 22.9 | 77.9 | 23.2 | 213.8 | 49 | 49 | NO
| NG | 4 | 69 | 69 | 14 | 126.6 | 0.56 | 50 | 78.7 | 22.9 | 78 | 22.9 | 213.3 | 49 | 49 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 66-010914
TR_B (available) | 66-004433
TR_A Rated kVA | 100
TR_B Rated kVA | 250
TR_A Baseline Loading% | 78.7
TR_B Baseline Loading% | 22.9
Total Scenarios Evaluated | 50
Feasible Scenarios | 9
--- Optimal Solution ---
Switch Parent Node | 36
Switch Child Node | 35
Tie Node (TR_A side) | 70
Tie Node (TR_B side) | 41
Tie Line Distance (m) | 82.2
Load Transferred (kW) | 22.85
TR_A Loading After (%) | 51
TR_B Loading After (%) | 26.4
Minimum Voltage (V) | 214.8