## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 73 | 72 | 32 | 49 | 1 | 50.74 | 95 | 78.7 | 31.7 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 73 | 74 | 9 | 12 | 144.6 | 15.77 | 50 | 78.7 | 31.7 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 72 | 75 | 32 | 49 | 1 | 50.11 | 95 | 78.7 | 31.7 | 19.1 | 57.7 | 220.5 | 193.1 | 193.1 | NO
| NG | 74 | 30 | 9 | 12 | 144.6 | 14.99 | 50 | 78.7 | 31.7 | 61.2 | 39.3 | 214.8 | 202.7 | 202.7 | NO
| NG | 75 | 19 | 32 | 49 | 1 | 48.85 | 95 | 78.7 | 31.7 | 20.5 | 56.9 | 220.5 | 193.6 | 193.6 | NO
| NG | 30 | 31 | 9 | 12 | 144.6 | 14.99 | 50 | 78.7 | 31.7 | 61.2 | 39.3 | 214.8 | 202.7 | 202.7 | NO
| NG | 19 | 23 | 32 | 49 | 1 | 48.85 | 95 | 78.7 | 31.7 | 0 | 56.9 | 0 | 193.6 | 0 | NO
| NG | 31 | 10 | 9 | 12 | 144.6 | 14.54 | 50 | 78.7 | 31.7 | 61.7 | 39 | 214.8 | 202.5 | 202.5 | NO
1 | OK | 23 | 22 | 32 | 49 | 1 | 31.95 | 95 | 78.7 | 31.7 | 40.3 | 47.4 | 218.7 | 211.8 | 211.8 | YES
| NG | 10 | 11 | 9 | 12 | 144.6 | 12.75 | 50 | 78.7 | 31.7 | 63.8 | 38 | 214.4 | 206.8 | 206.8 | NO
2 | OK | 22 | 34 | 32 | 49 | 1 | 31.95 | 95 | 78.7 | 31.7 | 40.3 | 47.4 | 218.7 | 211.8 | 211.8 | YES
| NG | 11 | 59 | 9 | 12 | 144.6 | 12.03 | 50 | 78.7 | 31.7 | 64.6 | 37.7 | 214.3 | 205.9 | 205.9 | NO
3 | OK | 34 | 33 | 32 | 49 | 1 | 31.28 | 95 | 78.7 | 31.7 | 41.1 | 47.1 | 218.6 | 213.1 | 213.1 | YES
| NG | 59 | 12 | 9 | 12 | 144.6 | 12.03 | 50 | 78.7 | 31.7 | 64.6 | 37.7 | 214.3 | 205.9 | 205.9 | NO
4 | OK | 33 | 36 | 32 | 49 | 1 | 30.34 | 95 | 78.7 | 31.7 | 42.2 | 46.5 | 218.6 | 213 | 213 | YES
| NG | 12 | 13 | 9 | 12 | 144.6 | 9.82 | 50 | 78.7 | 31.7 | 67.1 | 36.6 | 214.3 | 205.3 | 205.3 | NO
5 | OK | 36 | 35 | 32 | 49 | 1 | 22.85 | 95 | 78.7 | 31.7 | 51 | 42.8 | 218.2 | 214.4 | 214.4 | YES
6 | OK | 36 | 43 | 29 | 49 | 133.2 | 7.22 | 50 | 78.7 | 31.7 | 69.9 | 35.1 | 214.3 | 221 | 214.3 | YES
7 | OK | 13 | 14 | 9 | 12 | 144.6 | 6.47 | 50 | 78.7 | 31.7 | 70.6 | 34.8 | 214.3 | 215.1 | 214.3 | YES
8 | OK | 35 | 28 | 32 | 49 | 1 | 22.11 | 95 | 78.7 | 31.7 | 51.8 | 42.4 | 218.2 | 214.4 | 214.4 | YES
9 | OK | 43 | 39 | 29 | 49 | 133.2 | 7.22 | 50 | 78.7 | 31.7 | 69.9 | 35.1 | 214.3 | 221 | 214.3 | YES
10 | OK | 14 | 61 | 9 | 12 | 144.6 | 6.47 | 50 | 78.7 | 31.7 | 71 | 34.8 | 214.2 | 215.1 | 214.2 | YES
11 | OK | 28 | 26 | 32 | 49 | 1 | 12.46 | 95 | 78.7 | 31.7 | 63.5 | 36.6 | 214.1 | 219.5 | 214.1 | YES
12 | OK | 39 | 50 | 29 | 49 | 133.2 | 0.1 | 50 | 78.7 | 31.7 | 78.6 | 31.8 | 213.3 | 223.3 | 213.3 | YES
13 | OK | 61 | 62 | 9 | 12 | 144.6 | 5.94 | 50 | 78.7 | 31.7 | 71.6 | 34.6 | 214.1 | 217.5 | 214.1 | YES
14 | OK | 26 | 45 | 32 | 49 | 1 | 10.22 | 95 | 78.7 | 31.7 | 66.2 | 36.6 | 214.8 | 219.5 | 214.8 | YES
15 | OK | 62 | 63 | 9 | 12 | 144.6 | 5.4 | 50 | 78.7 | 31.7 | 72.2 | 34.3 | 214.1 | 217.4 | 214.1 | YES
16 | OK | 45 | 44 | 32 | 49 | 1 | 1.21 | 95 | 78.7 | 31.7 | 77.2 | 32.3 | 213.1 | 223.3 | 213.1 | YES
17 | ** OPTIMAL ** | 45 | 66 | 66 | 49 | 112.3 | 9.01 | 50 | 78.7 | 31.7 | 67.6 | 36 | 215 | 219.7 | 215 | YES
18 | OK | 63 | 64 | 9 | 12 | 144.6 | 5.4 | 50 | 78.7 | 31.7 | 72.2 | 34.3 | 214.1 | 217.4 | 214.1 | YES
19 | OK | 44 | 51 | 32 | 49 | 1 | 0.29 | 95 | 78.7 | 31.7 | 78.3 | 31.8 | 213.2 | 223.3 | 213.2 | YES
20 | OK | 66 | 58 | 58 | 49 | 115.6 | 8.41 | 50 | 78.7 | 31.7 | 68.4 | 35.7 | 214.2 | 219.6 | 214.2 | YES
21 | OK | 64 | 15 | 9 | 12 | 144.6 | 5.4 | 50 | 78.7 | 31.7 | 72.2 | 34.3 | 214.1 | 217.4 | 214.1 | YES
22 | OK | 58 | 46 | 46 | 49 | 122.5 | 7.93 | 50 | 78.7 | 31.7 | 68.4 | 35.5 | 214.2 | 219.9 | 214.2 | YES
23 | OK | 15 | 16 | 9 | 12 | 144.6 | 4.26 | 50 | 78.7 | 31.7 | 73.6 | 33.7 | 213.8 | 221.1 | 213.8 | YES
24 | OK | 46 | 47 | 47 | 49 | 139.3 | 6.37 | 50 | 78.7 | 31.7 | 70.9 | 34.7 | 213.4 | 220.5 | 213.4 | YES
25 | OK | 16 | 17 | 9 | 12 | 144.6 | 3.4 | 50 | 78.7 | 31.7 | 74.6 | 33.3 | 213.6 | 221.6 | 213.6 | YES
26 | OK | 47 | 48 | 48 | 49 | 160 | 4.05 | 50 | 78.7 | 31.7 | 73.7 | 33.6 | 213.8 | 222.6 | 213.8 | YES
27 | OK | 17 | 18 | 9 | 12 | 144.6 | 2.03 | 50 | 78.7 | 31.7 | 76.2 | 32.7 | 213.6 | 223.2 | 213.6 | YES
28 | OK | 18 | 9 | 9 | 12 | 144.6 | 1.33 | 50 | 78.7 | 31.7 | 77.1 | 32.3 | 213.6 | 223.2 | 213.6 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 66-010914
TR_B (available) | 66-016738
TR_A Rated kVA | 100
TR_B Rated kVA | 250
TR_A Baseline Loading% | 78.7
TR_B Baseline Loading% | 31.7
Total Scenarios Evaluated | 40
Feasible Scenarios | 28
--- Optimal Solution ---
Switch Parent Node | 45
Switch Child Node | 66
Tie Node (TR_A side) | 66
Tie Node (TR_B side) | 49
Tie Line Distance (m) | 112.3
Load Transferred (kW) | 9.01
TR_A Loading After (%) | 67.6
TR_B Loading After (%) | 36
Minimum Voltage (V) | 215