## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 13 | 14 | 27 | 43 | 12.6 | 37.58 | 50 | 77.2 | 21.3 | 33.1 | 41.7 | 224.2 | 129.6 | 129.6 | NO
1 | OK | 13 | 15 | 81 | 11 | 11.1 | 14.58 | 50 | 77.2 | 21.3 | 60.5 | 32.4 | 214.7 | 210.7 | 210.7 | YES
| NG | 13 | 11 | 23 | 37 | 37.8 | 14.11 | 50 | 77.2 | 21.3 | 60.9 | 25.3 | 214.8 | 204.4 | 204.4 | NO
| NG | 14 | 82 | 27 | 43 | 12.6 | 37.36 | 50 | 77.2 | 21.3 | 33.3 | 41.7 | 224.2 | 129.6 | 129.6 | NO
2 | OK | 15 | 10 | 81 | 11 | 11.1 | 14.58 | 50 | 77.2 | 21.3 | 60.5 | 32.4 | 214.7 | 210.7 | 210.7 | YES
| NG | 11 | 12 | 23 | 37 | 37.8 | 13.19 | 50 | 77.2 | 21.3 | 62 | 24.5 | 214.6 | 209.3 | 209.3 | NO
| NG | 82 | 24 | 27 | 43 | 12.6 | 37.16 | 50 | 77.2 | 21.3 | 33.3 | 41.7 | 224.2 | 129.6 | 129.6 | NO
3 | OK | 10 | 9 | 81 | 11 | 11.1 | 14.49 | 50 | 77.2 | 21.3 | 60.6 | 32.4 | 214.6 | 210.7 | 210.7 | YES
4 | OK | 12 | 69 | 23 | 37 | 37.8 | 9.99 | 50 | 77.2 | 21.3 | 65.6 | 24.2 | 214.5 | 211 | 211 | YES
| NG | 24 | 25 | 27 | 43 | 12.6 | 37.16 | 50 | 77.2 | 21.3 | 33.5 | 41.7 | 224.2 | 129.6 | 129.6 | NO
5 | OK | 9 | 71 | 81 | 11 | 11.1 | 13.64 | 50 | 77.2 | 21.3 | 61.5 | 31.1 | 214.4 | 210.4 | 210.4 | YES
6 | OK | 69 | 16 | 23 | 37 | 37.8 | 9.18 | 50 | 77.2 | 21.3 | 66.6 | 24.2 | 214.5 | 211 | 211 | YES
| NG | 25 | 26 | 26 | 43 | 34.2 | 31.19 | 50 | 77.2 | 21.3 | 40.4 | 48.8 | 224.2 | 177.6 | 177.6 | NO
| NG | 25 | 27 | 27 | 43 | 12.6 | 5.97 | 50 | 77.2 | 21.3 | 70.3 | 26.5 | 213.6 | 198 | 198 | NO
7 | OK | 71 | 89 | 81 | 11 | 11.1 | 11.79 | 50 | 77.2 | 21.3 | 63.7 | 30.3 | 214.3 | 210.6 | 210.6 | YES
8 | OK | 16 | 17 | 23 | 37 | 37.8 | 7.02 | 50 | 77.2 | 21.3 | 69.1 | 24.2 | 214.5 | 211 | 211 | YES
| NG | 26 | 29 | 29 | 43 | 36.1 | 28.69 | 50 | 77.2 | 21.3 | 43.3 | 46.6 | 224.2 | 175.7 | 175.7 | NO
| NG | 27 | 28 | 28 | 42 | 15.7 | 4.07 | 50 | 77.2 | 21.3 | 72.5 | 24.7 | 213.6 | 205.8 | 205.8 | NO
9 | OK | 89 | 2 | 81 | 11 | 11.1 | 11.09 | 50 | 77.2 | 21.3 | 63.7 | 29.7 | 214.3 | 211.5 | 211.5 | YES
10 | OK | 17 | 70 | 23 | 37 | 37.8 | 4.86 | 50 | 77.2 | 21.3 | 71.6 | 24.2 | 214.5 | 211 | 211 | YES
| NG | 29 | 30 | 30 | 43 | 53.6 | 8.2 | 50 | 77.2 | 21.3 | 67.5 | 28.1 | 216.2 | 193.2 | 193.2 | NO
| NG | 29 | 51 | 51 | 43 | 50.5 | 20.49 | 50 | 77.2 | 21.3 | 52.9 | 38.6 | 216.4 | 190.1 | 190.1 | NO
11 | OK | 2 | 1 | 81 | 11 | 11.1 | 11.09 | 50 | 77.2 | 21.3 | 64.5 | 28.9 | 214.3 | 211.4 | 211.4 | YES
12 | OK | 70 | 18 | 23 | 37 | 37.8 | 2.4 | 50 | 77.2 | 21.3 | 73.8 | 22.8 | 214.3 | 217.3 | 214.3 | YES
| NG | 30 | 31 | 31 | 43 | 78.1 | 8.2 | 50 | 77.2 | 21.3 | 67.5 | 28.1 | 216.2 | 193.4 | 193.4 | NO
| NG | 51 | 52 | 52 | 43 | 74.8 | 20.42 | 50 | 77.2 | 21.3 | 53 | 38.5 | 216.6 | 190.1 | 190.1 | NO
13 | OK | 1 | 0 | 81 | 11 | 11.1 | 2.94 | 50 | 77.2 | 21.3 | 73.8 | 23.5 | 213.7 | 213.8 | 213.7 | YES
14 | OK | 1 | 91 | 4 | 16 | 33.5 | 6.99 | 50 | 77.2 | 21.3 | 69.2 | 23 | 214.2 | 217.6 | 214.2 | YES
15 | OK | 18 | 19 | 23 | 37 | 37.8 | 2.14 | 50 | 77.2 | 21.3 | 74.7 | 22.8 | 214.1 | 217.3 | 214.1 | YES
| NG | 31 | 32 | 32 | 43 | 114.4 | 7.7 | 50 | 77.2 | 21.3 | 68 | 27.7 | 216.3 | 195.5 | 195.5 | NO
| NG | 52 | 43 | 43 | 8 | 79.4 | 20.42 | 50 | 77.2 | 21.3 | 53 | 38.5 | 216.6 | 190.1 | 190.1 | NO
16 | OK | 0 | 78 | 81 | 11 | 11.1 | 0.17 | 50 | 77.2 | 21.3 | 77.1 | 21.4 | 213.7 | 217.3 | 213.7 | YES
17 | OK | 91 | 3 | 4 | 16 | 33.5 | 6.99 | 50 | 77.2 | 21.3 | 69.2 | 23 | 214.2 | 217.6 | 214.2 | YES
18 | OK | 19 | 72 | 23 | 37 | 37.8 | 1.7 | 50 | 77.2 | 21.3 | 75.2 | 22.4 | 214 | 217.3 | 214 | YES
| NG | 43 | 44 | 44 | 8 | 95.5 | 20.34 | 50 | 77.2 | 21.3 | 53.1 | 38.4 | 216.5 | 190.5 | 190.5 | NO
19 | OK | 78 | 73 | 81 | 11 | 11.1 | 0.17 | 50 | 77.2 | 21.3 | 77.1 | 21.4 | 213.7 | 217.3 | 213.7 | YES
20 | OK | 3 | 4 | 4 | 16 | 33.5 | 5.3 | 50 | 77.2 | 21.3 | 71.1 | 23 | 214.2 | 217.6 | 214.2 | YES
21 | OK | 72 | 20 | 23 | 37 | 37.8 | 1.7 | 50 | 77.2 | 21.3 | 75.2 | 22.4 | 214 | 217.3 | 214 | YES
| NG | 44 | 85 | 85 | 8 | 96.9 | 20.34 | 50 | 77.2 | 21.3 | 53.1 | 38.4 | 216.5 | 190.6 | 190.6 | NO
22 | OK | 73 | 74 | 74 | 10 | 25.3 | 0.15 | 50 | 77.2 | 21.3 | 77.1 | 21.4 | 213.7 | 217.3 | 213.7 | YES
23 | OK | 73 | 75 | 81 | 11 | 11.1 | 0.02 | 50 | 77.2 | 21.3 | 77.2 | 21.3 | 213.7 | 217.3 | 213.7 | YES
24 | OK | 4 | 5 | 5 | 16 | 40.8 | 2.57 | 50 | 77.2 | 21.3 | 74.3 | 22.2 | 214 | 217.5 | 214 | YES
25 | OK | 20 | 21 | 23 | 37 | 37.8 | 1.11 | 50 | 77.2 | 21.3 | 75.9 | 22.1 | 213.9 | 217.3 | 213.9 | YES
| NG | 85 | 36 | 36 | 8 | 101.5 | 18.98 | 50 | 77.2 | 21.3 | 54.7 | 37.1 | 216.5 | 196.5 | 196.5 | NO
26 | OK | 74 | 76 | 76 | 10 | 30.5 | 0.15 | 50 | 77.2 | 21.3 | 77.1 | 21.3 | 213.7 | 217.3 | 213.7 | YES
27 | OK | 75 | 81 | 81 | 11 | 11.1 | 0.02 | 50 | 77.2 | 21.3 | 77.2 | 21.3 | 213.7 | 217.3 | 213.7 | YES
28 | OK | 5 | 47 | 47 | 16 | 43.5 | 2.55 | 50 | 77.2 | 21.3 | 74.3 | 22.2 | 214 | 217.5 | 214 | YES
29 | OK | 21 | 22 | 23 | 37 | 37.8 | 0.87 | 50 | 77.2 | 21.3 | 76.2 | 22 | 213.9 | 217.3 | 213.9 | YES
| NG | 36 | 34 | 34 | 8 | 115.8 | 18.98 | 50 | 77.2 | 21.3 | 54.7 | 37.1 | 216.5 | 196.6 | 196.6 | NO
30 | OK | 47 | 48 | 48 | 16 | 71.2 | 2.42 | 50 | 77.2 | 21.3 | 74.4 | 22.1 | 213.9 | 217.4 | 213.9 | YES
31 | OK | 22 | 23 | 23 | 37 | 37.8 | 0.87 | 50 | 77.2 | 21.3 | 76.2 | 21.3 | 213.9 | 217.3 | 213.9 | YES
| NG | 34 | 35 | 35 | 8 | 132.2 | 16.56 | 50 | 77.2 | 21.3 | 57.5 | 35 | 215.1 | 195.7 | 195.7 | NO
32 | ** OPTIMAL ** | 34 | 63 | 63 | 8 | 122.2 | 2.42 | 50 | 77.2 | 21.3 | 74.4 | 23.2 | 215.2 | 215.8 | 215.2 | YES
33 | OK | 48 | 45 | 8 | 32 | 81.7 | 2.27 | 50 | 77.2 | 21.3 | 74.6 | 21.7 | 213.9 | 217.3 | 213.9 | YES
34 | OK | 45 | 46 | 8 | 32 | 81.7 | 1.94 | 50 | 77.2 | 21.3 | 75 | 21.7 | 213.8 | 217.3 | 213.8 | YES
35 | OK | 46 | 90 | 8 | 32 | 81.7 | 1.31 | 50 | 77.2 | 21.3 | 75.7 | 21.7 | 213.7 | 217.3 | 213.7 | YES
36 | OK | 90 | 6 | 8 | 32 | 81.7 | 1.31 | 50 | 77.2 | 21.3 | 75.7 | 21.7 | 213.7 | 217.3 | 213.7 | YES
37 | OK | 6 | 7 | 8 | 32 | 81.7 | 0.73 | 50 | 77.2 | 21.3 | 76.4 | 21.3 | 213.7 | 217.3 | 213.7 | YES
38 | OK | 7 | 8 | 8 | 32 | 81.7 | 0.73 | 50 | 77.2 | 21.3 | 76.4 | 21.3 | 213.7 | 217.3 | 213.7 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 66-011386
TR_B (available) | 23-000708
TR_A Rated kVA | 100
TR_B Rated kVA | 160
TR_A Baseline Loading% | 77.2
TR_B Baseline Loading% | 21.3
Total Scenarios Evaluated | 59
Feasible Scenarios | 38
--- Optimal Solution ---
Switch Parent Node | 34
Switch Child Node | 63
Tie Node (TR_A side) | 63
Tie Node (TR_B side) | 8
Tie Line Distance (m) | 122.2
Load Transferred (kW) | 2.42
TR_A Loading After (%) | 74.4
TR_B Loading After (%) | 23.2
Minimum Voltage (V) | 215.2