## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 13 | 15 | 15 | 42 | 194.4 | 14.58 | 50 | 77.2 | 49.8 | 60.5 | 68.8 | 214.7 | 199.8 | 199.8 | NO
| NG | 13 | 11 | 11 | 42 | 186.2 | 14.11 | 50 | 77.2 | 49.8 | 60.9 | 68.5 | 214.8 | 195.9 | 195.9 | NO
| NG | 15 | 10 | 10 | 42 | 200.3 | 14.58 | 50 | 77.2 | 49.8 | 60.5 | 68.8 | 214.7 | 199.7 | 199.7 | NO
| NG | 11 | 12 | 12 | 42 | 186.4 | 13.19 | 50 | 77.2 | 49.8 | 62 | 67.1 | 214.6 | 197.1 | 197.1 | NO
| NG | 10 | 9 | 9 | 42 | 221.7 | 14.49 | 50 | 77.2 | 49.8 | 60.6 | 68.7 | 214.6 | 199.6 | 199.6 | NO
| NG | 12 | 69 | 69 | 42 | 191.9 | 9.99 | 50 | 77.2 | 49.8 | 65.6 | 62.8 | 214.5 | 203.8 | 203.8 | NO
| NG | 9 | 71 | 71 | 42 | 224.6 | 13.64 | 50 | 77.2 | 49.8 | 61.5 | 66.5 | 214.4 | 198.5 | 198.5 | NO
| NG | 69 | 16 | 16 | 42 | 192.8 | 9.18 | 50 | 77.2 | 49.8 | 66.6 | 61.8 | 214.5 | 203.3 | 203.3 | NO
| NG | 25 | 27 | 27 | 42 | 138.4 | 5.97 | 50 | 77.2 | 49.8 | 70.3 | 57.7 | 213.6 | 201.8 | 201.8 | NO
| NG | 71 | 89 | 89 | 42 | 244.2 | 11.79 | 50 | 77.2 | 49.8 | 63.7 | 65.1 | 214.3 | 199.2 | 199.2 | NO
| NG | 16 | 17 | 17 | 42 | 228 | 7.02 | 50 | 77.2 | 49.8 | 69.1 | 58.9 | 214.5 | 203.4 | 203.4 | NO
| NG | 26 | 29 | 63 | 42 | 3.3 | 28.69 | 50 | 77.2 | 49.8 | 43.3 | 89.9 | 224.2 | 166.5 | 166.5 | NO
| NG | 27 | 28 | 28 | 42 | 147.7 | 4.07 | 50 | 77.2 | 49.8 | 72.5 | 55 | 213.6 | 208.9 | 208.9 | NO
| NG | 89 | 2 | 2 | 42 | 252 | 11.09 | 50 | 77.2 | 49.8 | 63.7 | 64.1 | 214.3 | 202.4 | 202.4 | NO
| NG | 29 | 30 | 55 | 21 | 76 | 8.2 | 50 | 77.2 | 49.8 | 67.5 | 60.7 | 216.2 | 197.5 | 197.5 | NO
| NG | 29 | 51 | 63 | 42 | 3.3 | 20.49 | 50 | 77.2 | 49.8 | 52.9 | 76.5 | 216.4 | 201.9 | 201.9 | NO
| NG | 2 | 1 | 91 | 42 | 254.9 | 11.09 | 50 | 77.2 | 49.8 | 64.5 | 62.6 | 214.3 | 202 | 202 | NO
| NG | 30 | 31 | 55 | 21 | 76 | 8.2 | 50 | 77.2 | 49.8 | 67.5 | 60.7 | 216.2 | 197.5 | 197.5 | NO
| NG | 51 | 52 | 63 | 42 | 3.3 | 20.42 | 50 | 77.2 | 49.8 | 53 | 76.4 | 216.6 | 201.8 | 201.8 | NO
1 | OK | 1 | 91 | 91 | 42 | 254.9 | 6.99 | 50 | 77.2 | 49.8 | 69.2 | 58.6 | 214.2 | 210.6 | 210.6 | YES
| NG | 31 | 32 | 55 | 21 | 76 | 7.7 | 50 | 77.2 | 49.8 | 68 | 60 | 216.3 | 199 | 199 | NO
| NG | 52 | 43 | 63 | 42 | 3.3 | 20.42 | 50 | 77.2 | 49.8 | 53 | 76.4 | 216.6 | 201.8 | 201.8 | NO
2 | OK | 91 | 3 | 3 | 42 | 258 | 6.99 | 50 | 77.2 | 49.8 | 69.2 | 58.6 | 214.2 | 210.9 | 210.9 | YES
| NG | 32 | 49 | 55 | 21 | 76 | 6.49 | 50 | 77.2 | 49.8 | 69.5 | 58.2 | 216.4 | 202.6 | 202.6 | NO
| NG | 43 | 44 | 63 | 42 | 3.3 | 20.34 | 50 | 77.2 | 49.8 | 53.1 | 76.3 | 216.5 | 201.8 | 201.8 | NO
| NG | 3 | 4 | 4 | 42 | 264.8 | 5.3 | 50 | 77.2 | 49.8 | 71.1 | 56.5 | 214.2 | 209.7 | 209.7 | NO
| NG | 49 | 50 | 55 | 21 | 76 | 6.4 | 50 | 77.2 | 49.8 | 69.6 | 58.1 | 216.4 | 202.9 | 202.9 | NO
| NG | 44 | 85 | 63 | 42 | 3.3 | 20.34 | 50 | 77.2 | 49.8 | 53.1 | 76.3 | 216.5 | 201.8 | 201.8 | NO
| NG | 50 | 42 | 55 | 21 | 76 | 6.4 | 50 | 77.2 | 49.8 | 69.6 | 58.1 | 216.4 | 202.9 | 202.9 | NO
| NG | 85 | 36 | 63 | 42 | 3.3 | 18.98 | 50 | 77.2 | 49.8 | 54.7 | 74.5 | 216.5 | 204.3 | 204.3 | NO
3 | OK | 42 | 33 | 33 | 15 | 124.5 | 0.87 | 50 | 77.2 | 49.8 | 76.2 | 50.9 | 214.1 | 216.4 | 214.1 | YES
| NG | 42 | 57 | 55 | 21 | 76 | 4.83 | 50 | 77.2 | 49.8 | 71.4 | 56.2 | 215.6 | 203.6 | 203.6 | NO
| NG | 36 | 34 | 63 | 42 | 3.3 | 18.98 | 50 | 77.2 | 49.8 | 54.7 | 74.5 | 216.5 | 204.3 | 204.3 | NO
4 | OK | 33 | 53 | 53 | 16 | 132 | 0.87 | 50 | 77.2 | 49.8 | 76.2 | 50.2 | 214.1 | 216.3 | 214.1 | YES
5 | OK | 57 | 58 | 58 | 22 | 139.8 | 1.73 | 50 | 77.2 | 49.8 | 75.1 | 52 | 215.9 | 213.3 | 213.3 | YES
| NG | 57 | 67 | 55 | 21 | 76 | 2.93 | 50 | 77.2 | 49.8 | 73.5 | 53.6 | 215.8 | 208.9 | 208.9 | NO
| NG | 34 | 35 | 41 | 84 | 50.1 | 16.56 | 50 | 77.2 | 49.8 | 57.5 | 72.6 | 215.1 | 187.3 | 187.3 | NO
6 | OK | 34 | 63 | 63 | 42 | 3.3 | 2.42 | 50 | 77.2 | 49.8 | 74.4 | 52.9 | 215.2 | 210.9 | 210.9 | YES
7 | OK | 53 | 54 | 54 | 22 | 179 | 0.19 | 50 | 77.2 | 49.8 | 77 | 50.1 | 214 | 216.6 | 214 | YES
8 | OK | 58 | 79 | 79 | 22 | 145.8 | 1.73 | 50 | 77.2 | 49.8 | 75.1 | 52 | 215.9 | 213.3 | 213.3 | YES
| NG | 67 | 83 | 55 | 21 | 76 | 2.93 | 50 | 77.2 | 49.8 | 73.7 | 53.6 | 215.8 | 208.9 | 208.9 | NO
| NG | 35 | 37 | 41 | 84 | 50.1 | 9.55 | 50 | 77.2 | 49.8 | 65.8 | 62.6 | 215.7 | 195.7 | 195.7 | NO
9 | OK | 54 | 66 | 66 | 23 | 180.8 | 0.19 | 50 | 77.2 | 49.8 | 77 | 49.8 | 214 | 217 | 214 | YES
10 | OK | 79 | 80 | 80 | 24 | 164.3 | 1.51 | 50 | 77.2 | 49.8 | 75.4 | 51.7 | 215.9 | 214.5 | 214.5 | YES
| NG | 83 | 55 | 55 | 21 | 76 | 2.91 | 50 | 77.2 | 49.8 | 73.7 | 53.6 | 215.8 | 208.9 | 208.9 | NO
| NG | 37 | 38 | 41 | 84 | 50.1 | 8.56 | 50 | 77.2 | 49.8 | 67 | 61.3 | 215.1 | 194.6 | 194.6 | NO
11 | OK | 80 | 87 | 87 | 31 | 177.7 | 0.07 | 50 | 77.2 | 49.8 | 77.2 | 49.9 | 213.8 | 216.9 | 213.8 | YES
12 | OK | 55 | 56 | 61 | 70 | 127.7 | 2.91 | 50 | 77.2 | 49.8 | 73.7 | 49.8 | 215.8 | 217 | 215.8 | YES
13 | OK | 38 | 59 | 41 | 84 | 50.1 | 2.46 | 50 | 77.2 | 49.8 | 74.3 | 53 | 215.2 | 210.2 | 210.2 | YES
14 | OK | 87 | 88 | 88 | 31 | 178.5 | 0.07 | 50 | 77.2 | 49.8 | 77.2 | 49.8 | 213.8 | 217 | 213.8 | YES
15 | OK | 56 | 86 | 61 | 70 | 127.7 | 2.75 | 50 | 77.2 | 49.8 | 73.9 | 49.8 | 215.8 | 217 | 215.8 | YES
16 | OK | 59 | 60 | 41 | 84 | 50.1 | 1.9 | 50 | 77.2 | 49.8 | 75 | 52.3 | 214.9 | 212.5 | 212.5 | YES
17 | OK | 86 | 84 | 61 | 70 | 127.7 | 2.75 | 50 | 77.2 | 49.8 | 73.9 | 49.8 | 215.8 | 217 | 215.8 | YES
18 | OK | 60 | 77 | 41 | 84 | 50.1 | 0.94 | 50 | 77.2 | 49.8 | 76.1 | 51 | 214.3 | 215.7 | 214.3 | YES
19 | OK | 84 | 68 | 61 | 70 | 127.7 | 2.53 | 50 | 77.2 | 49.8 | 74.1 | 49.8 | 215.9 | 217 | 215.9 | YES
20 | OK | 77 | 39 | 41 | 84 | 50.1 | 0.94 | 50 | 77.2 | 49.8 | 76.1 | 51 | 214.3 | 215.7 | 214.3 | YES
21 | OK | 68 | 65 | 61 | 70 | 127.7 | 1.74 | 50 | 77.2 | 49.8 | 75.1 | 49.8 | 215.9 | 217 | 215.9 | YES
22 | OK | 39 | 40 | 41 | 84 | 50.1 | 0.59 | 50 | 77.2 | 49.8 | 76.5 | 50.6 | 214.1 | 216.8 | 214.1 | YES
23 | OK | 65 | 61 | 61 | 70 | 127.7 | 1.67 | 50 | 77.2 | 49.8 | 75.2 | 49.8 | 215.9 | 217 | 215.9 | YES
24 | ** OPTIMAL ** | 61 | 62 | 62 | 70 | 145.7 | 1.67 | 50 | 77.2 | 49.8 | 75.2 | 49.8 | 215.9 | 217 | 215.9 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 66-011386
TR_B (available) | 55-940595
TR_A Rated kVA | 100
TR_B Rated kVA | 100
TR_A Baseline Loading% | 77.2
TR_B Baseline Loading% | 49.8
Total Scenarios Evaluated | 60
Feasible Scenarios | 24
--- Optimal Solution ---
Switch Parent Node | 61
Switch Child Node | 62
Tie Node (TR_A side) | 62
Tie Node (TR_B side) | 70
Tie Line Distance (m) | 145.7
Load Transferred (kW) | 1.67
TR_A Loading After (%) | 75.2
TR_B Loading After (%) | 49.8
Minimum Voltage (V) | 215.9