## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 30 | 29 | 6 | 50 | 74.7 | 18.44 | 50 | 131.6 | 16.1 | 56.1 | 38.7 | 213.9 | 209.1 | 209.1 | NO
| NG | 29 | 28 | 6 | 50 | 74.7 | 18.44 | 50 | 131.6 | 16.1 | 56.1 | 38.7 | 213.9 | 209.1 | 209.1 | NO
| NG | 28 | 19 | 6 | 50 | 74.7 | 17.8 | 50 | 131.6 | 16.1 | 58.5 | 37.9 | 213.4 | 209.6 | 209.6 | NO
1 | OK | 19 | 16 | 6 | 50 | 74.7 | 16.88 | 50 | 131.6 | 16.1 | 58.5 | 36.7 | 213.4 | 210.3 | 210.3 | YES
2 | ** OPTIMAL ** | 16 | 20 | 6 | 50 | 74.7 | 15.68 | 50 | 131.6 | 16.1 | 66.6 | 35.2 | 211.7 | 211.2 | 211.2 | YES
3 | OK | 20 | 17 | 6 | 50 | 74.7 | 15.68 | 50 | 131.6 | 16.1 | 66.6 | 35.2 | 211.7 | 211.2 | 211.2 | YES
4 | OK | 17 | 15 | 6 | 50 | 74.7 | 15.68 | 50 | 131.6 | 16.1 | 66.6 | 35.2 | 211.7 | 211.2 | 211.2 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 66-012422
TR_B (available) | 67-023645
TR_A Rated kVA | 30
TR_B Rated kVA | 100
TR_A Baseline Loading% | 131.6
TR_B Baseline Loading% | 16.1
Total Scenarios Evaluated | 7
Feasible Scenarios | 4
--- Optimal Solution ---
Switch Parent Node | 16
Switch Child Node | 20
Tie Node (TR_A side) | 6
Tie Node (TR_B side) | 50
Tie Line Distance (m) | 74.7
Load Transferred (kW) | 15.68
TR_A Loading After (%) | 66.6
TR_B Loading After (%) | 35.2
Minimum Voltage (V) | 211.2