## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 43 | 44 | 30 | 55 | 120.1 | 16.02 | 50 | 79.1 | 20.7 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 43 | 32 | 53 | 58 | 104.1 | 18.27 | 50 | 79.1 | 20.7 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 44 | 45 | 30 | 55 | 120.1 | 16.02 | 50 | 79.1 | 20.7 | 48.3 | 28.3 | 20 | 216.4 | 20 | NO
1 | OK | 32 | 31 | 53 | 58 | 104.1 | 18.27 | 50 | 79.1 | 20.7 | 36.9 | 23.2 | 223.9 | 213.5 | 213.5 | YES
2 | OK | 45 | 35 | 30 | 55 | 120.1 | 16.02 | 50 | 79.1 | 20.7 | 42.1 | 28.3 | 223.4 | 216.4 | 216.4 | YES
3 | OK | 31 | 0 | 53 | 58 | 104.1 | 18.27 | 50 | 79.1 | 20.7 | 36.9 | 23.2 | 223.9 | 213.5 | 213.5 | YES
4 | OK | 35 | 25 | 30 | 55 | 120.1 | 16.02 | 50 | 79.1 | 20.7 | 42.1 | 28.3 | 223.4 | 216.4 | 216.4 | YES
5 | OK | 0 | 1 | 53 | 58 | 104.1 | 7.43 | 50 | 79.1 | 20.7 | 57.1 | 22.2 | 221.1 | 214.9 | 214.9 | YES
| NG | 0 | 16 | 51 | 98 | 232.2 | 8.54 | 50 | 79.1 | 20.7 | 59.2 | 21.8 | 222.3 | 209.8 | 209.8 | NO
6 | ** OPTIMAL ** | 0 | 36 | 40 | 98 | 187.4 | 0.9 | 50 | 79.1 | 20.7 | 77 | 21.2 | 219.9 | 217.3 | 217.3 | YES
7 | OK | 25 | 8 | 34 | 77 | 121.2 | 11.88 | 50 | 79.1 | 20.7 | 51.6 | 26.3 | 222.4 | 216.6 | 216.6 | YES
8 | OK | 25 | 23 | 30 | 55 | 120.1 | 4.14 | 50 | 79.1 | 20.7 | 69.5 | 22.7 | 220.8 | 216.8 | 216.8 | YES
9 | OK | 1 | 2 | 53 | 58 | 104.1 | 4.61 | 50 | 79.1 | 20.7 | 68.4 | 21 | 220.3 | 216.6 | 216.6 | YES
| NG | 16 | 15 | 51 | 98 | 232.2 | 7.86 | 50 | 79.1 | 20.7 | 60.8 | 21.8 | 222.3 | 209.8 | 209.8 | NO
10 | OK | 36 | 37 | 38 | 98 | 232.4 | 0.47 | 50 | 79.1 | 20.7 | 78 | 21 | 219.7 | 217.2 | 217.2 | YES
11 | OK | 36 | 39 | 40 | 98 | 187.4 | 0.43 | 50 | 79.1 | 20.7 | 78 | 21 | 219.9 | 217 | 217 | YES
12 | OK | 8 | 9 | 34 | 77 | 121.2 | 11.88 | 50 | 79.1 | 20.7 | 51.6 | 26.3 | 222.4 | 216.6 | 216.6 | YES
13 | OK | 23 | 24 | 30 | 55 | 120.1 | 2.8 | 50 | 79.1 | 20.7 | 72.6 | 22 | 220.5 | 216.9 | 216.9 | YES
14 | OK | 2 | 3 | 53 | 58 | 104.1 | 2.92 | 50 | 79.1 | 20.7 | 72.3 | 21 | 220.3 | 216.6 | 216.6 | YES
15 | OK | 2 | 4 | 7 | 58 | 168.8 | 1.69 | 50 | 79.1 | 20.7 | 75.2 | 21.5 | 219.7 | 217.2 | 217.2 | YES
| NG | 15 | 19 | 51 | 98 | 232.2 | 4.69 | 50 | 79.1 | 20.7 | 68.1 | 21.8 | 221.1 | 209.8 | 209.8 | NO
16 | OK | 15 | 20 | 20 | 55 | 280.4 | 3.17 | 50 | 79.1 | 20.7 | 71.7 | 22.2 | 221 | 216.9 | 216.9 | YES
17 | OK | 39 | 40 | 40 | 98 | 187.4 | 0.43 | 50 | 79.1 | 20.7 | 78 | 20.7 | 219.9 | 216.9 | 216.9 | YES
18 | OK | 9 | 28 | 34 | 77 | 121.2 | 10.06 | 50 | 79.1 | 20.7 | 55.8 | 25.4 | 222.3 | 216.7 | 216.7 | YES
19 | OK | 3 | 5 | 53 | 58 | 104.1 | 2.61 | 50 | 79.1 | 20.7 | 73 | 21 | 220.3 | 216.6 | 216.6 | YES
20 | OK | 19 | 18 | 51 | 98 | 232.2 | 4.04 | 50 | 79.1 | 20.7 | 69.6 | 21.4 | 221.1 | 212.6 | 212.6 | YES
21 | OK | 28 | 29 | 34 | 77 | 121.2 | 3.69 | 50 | 79.1 | 20.7 | 70.5 | 22.4 | 221 | 216.9 | 216.9 | YES
22 | OK | 28 | 13 | 13 | 77 | 255.6 | 6.37 | 50 | 79.1 | 20.7 | 64.3 | 23.7 | 221.1 | 216.7 | 216.7 | YES
23 | OK | 5 | 6 | 53 | 58 | 104.1 | 1.51 | 50 | 79.1 | 20.7 | 75.5 | 20.9 | 220.1 | 216.7 | 216.7 | YES
24 | OK | 18 | 26 | 51 | 98 | 232.2 | 3.69 | 50 | 79.1 | 20.7 | 70.4 | 21.4 | 220.9 | 212.6 | 212.6 | YES
25 | OK | 29 | 33 | 34 | 77 | 121.2 | 3.61 | 50 | 79.1 | 20.7 | 70.7 | 22.4 | 221 | 216.9 | 216.9 | YES
26 | OK | 6 | 52 | 53 | 58 | 104.1 | 1.22 | 50 | 79.1 | 20.7 | 76.2 | 20.7 | 220.1 | 216.9 | 216.9 | YES
27 | OK | 26 | 22 | 51 | 98 | 232.2 | 2.92 | 50 | 79.1 | 20.7 | 70.4 | 21.4 | 220.9 | 212.6 | 212.6 | YES
28 | OK | 22 | 21 | 51 | 98 | 232.2 | 0.41 | 50 | 79.1 | 20.7 | 78.1 | 20.7 | 219.9 | 216.9 | 216.9 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 66-012726
TR_B (available) | 57-010175
TR_A Rated kVA | 50
TR_B Rated kVA | 250
TR_A Baseline Loading% | 79.1
TR_B Baseline Loading% | 20.7
Total Scenarios Evaluated | 34
Feasible Scenarios | 28
--- Optimal Solution ---
Switch Parent Node | 0
Switch Child Node | 36
Tie Node (TR_A side) | 40
Tie Node (TR_B side) | 98
Tie Line Distance (m) | 187.4
Load Transferred (kW) | 0.9
TR_A Loading After (%) | 77
TR_B Loading After (%) | 21.2
Minimum Voltage (V) | 217.3