## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 43 | 44 | 47 | 92 | 83 | 16.02 | 50 | 79.1 | 40.3 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 43 | 32 | 41 | 37 | 2.7 | 18.27 | 50 | 79.1 | 40.3 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 44 | 45 | 47 | 92 | 83 | 16.02 | 50 | 79.1 | 40.3 | 0 | 48.2 | 20 | 207.4 | 20 | NO
| NG | 32 | 31 | 41 | 37 | 2.7 | 18.27 | 50 | 79.1 | 40.3 | 36.9 | 49.6 | 223.9 | 201 | 201 | NO
| NG | 45 | 35 | 47 | 92 | 83 | 16.02 | 50 | 79.1 | 40.3 | 42.1 | 48.2 | 223.4 | 207.4 | 207.4 | NO
| NG | 31 | 0 | 41 | 37 | 2.7 | 18.27 | 50 | 79.1 | 40.3 | 36.9 | 49.6 | 223.9 | 201 | 201 | NO
| NG | 35 | 25 | 47 | 92 | 83 | 16.02 | 50 | 79.1 | 40.3 | 42.1 | 48.2 | 223.4 | 207.4 | 207.4 | NO
1 | OK | 0 | 1 | 1 | 37 | 131.8 | 7.43 | 50 | 79.1 | 40.3 | 57.1 | 43.9 | 221.1 | 218 | 218 | YES
| NG | 0 | 16 | 41 | 37 | 2.7 | 8.54 | 50 | 79.1 | 40.3 | 59.2 | 44.2 | 222.3 | 207.5 | 207.5 | NO
2 | OK | 25 | 8 | 47 | 92 | 83 | 11.88 | 50 | 79.1 | 40.3 | 51.6 | 46 | 222.4 | 212.5 | 212.5 | YES
| NG | 16 | 15 | 41 | 37 | 2.7 | 7.86 | 50 | 79.1 | 40.3 | 60.8 | 44.2 | 222.3 | 207.5 | 207.5 | NO
3 | OK | 8 | 9 | 47 | 92 | 83 | 11.88 | 50 | 79.1 | 40.3 | 51.6 | 46 | 222.4 | 212.5 | 212.5 | YES
4 | OK | 15 | 19 | 19 | 37 | 107 | 4.69 | 50 | 79.1 | 40.3 | 68.1 | 42.6 | 221.1 | 213.4 | 213.4 | YES
5 | OK | 15 | 20 | 41 | 37 | 2.7 | 3.17 | 50 | 79.1 | 40.3 | 71.7 | 41.8 | 221 | 214 | 214 | YES
6 | OK | 9 | 28 | 47 | 92 | 83 | 10.06 | 50 | 79.1 | 40.3 | 55.8 | 45.1 | 222.3 | 212.8 | 212.8 | YES
7 | OK | 19 | 18 | 18 | 37 | 130.9 | 4.04 | 50 | 79.1 | 40.3 | 69.6 | 42.3 | 221.1 | 213.2 | 213.2 | YES
8 | OK | 20 | 50 | 41 | 37 | 2.7 | 3.17 | 50 | 79.1 | 40.3 | 71.7 | 41.8 | 221 | 214 | 214 | YES
9 | OK | 28 | 13 | 47 | 92 | 83 | 6.37 | 50 | 79.1 | 40.3 | 64.3 | 43.3 | 221.1 | 219.3 | 219.3 | YES
10 | OK | 50 | 48 | 48 | 37 | 72.1 | 1.33 | 50 | 79.1 | 40.3 | 75.9 | 40.9 | 220.4 | 216.7 | 216.7 | YES
11 | OK | 50 | 42 | 41 | 37 | 2.7 | 1.84 | 50 | 79.1 | 40.3 | 74.8 | 41.2 | 220.3 | 217.2 | 217.2 | YES
12 | OK | 13 | 12 | 47 | 92 | 83 | 5.87 | 50 | 79.1 | 40.3 | 65.4 | 43 | 220.9 | 219.4 | 219.4 | YES
13 | OK | 12 | 27 | 47 | 92 | 83 | 5.05 | 50 | 79.1 | 40.3 | 67.3 | 42.7 | 220.9 | 219.4 | 219.4 | YES
14 | OK | 27 | 17 | 47 | 92 | 83 | 4.64 | 50 | 79.1 | 40.3 | 68.3 | 42.5 | 220.9 | 219.4 | 219.4 | YES
15 | OK | 17 | 11 | 47 | 92 | 83 | 4.64 | 50 | 79.1 | 40.3 | 68.3 | 42.5 | 220.9 | 219.4 | 219.4 | YES
16 | OK | 11 | 10 | 47 | 92 | 83 | 3.43 | 50 | 79.1 | 40.3 | 71.1 | 41.9 | 220.9 | 219.4 | 219.4 | YES
17 | ** OPTIMAL ** | 10 | 14 | 47 | 92 | 83 | 1.25 | 50 | 79.1 | 40.3 | 76.1 | 40.8 | 220 | 219.5 | 219.5 | YES
18 | OK | 14 | 46 | 47 | 92 | 83 | 1.25 | 50 | 79.1 | 40.3 | 76.1 | 40.8 | 220 | 219.5 | 219.5 | YES
19 | OK | 46 | 47 | 47 | 92 | 83 | 0.91 | 50 | 79.1 | 40.3 | 76.9 | 40.7 | 219.4 | 219.6 | 219.4 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 66-012726
TR_B (available) | 60-027230
TR_A Rated kVA | 50
TR_B Rated kVA | 250
TR_A Baseline Loading% | 79.1
TR_B Baseline Loading% | 40.3
Total Scenarios Evaluated | 28
Feasible Scenarios | 19
--- Optimal Solution ---
Switch Parent Node | 10
Switch Child Node | 14
Tie Node (TR_A side) | 47
Tie Node (TR_B side) | 92
Tie Line Distance (m) | 83
Load Transferred (kW) | 1.25
TR_A Loading After (%) | 76.1
TR_B Loading After (%) | 40.8
Minimum Voltage (V) | 219.5