## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 43 | 44 | 47 | 23 | 14 | 16.02 | 50 | 79.1 | 54.7 | 42.1 | 74 | 223.4 | 209.8 | 209.8 | NO
| NG | 44 | 45 | 47 | 23 | 14 | 16.02 | 50 | 79.1 | 54.7 | 48.3 | 74 | 20 | 209.8 | 20 | NO
| NG | 45 | 35 | 47 | 23 | 14 | 16.02 | 50 | 79.1 | 54.7 | 42.1 | 74 | 223.4 | 209.8 | 209.8 | NO
| NG | 35 | 25 | 47 | 23 | 14 | 16.02 | 50 | 79.1 | 54.7 | 42.1 | 74 | 223.4 | 209.8 | 209.8 | NO
1 | OK | 25 | 8 | 47 | 23 | 14 | 11.88 | 50 | 79.1 | 54.7 | 51.6 | 68.8 | 222.4 | 214.9 | 214.9 | YES
2 | OK | 8 | 9 | 47 | 23 | 14 | 11.88 | 50 | 79.1 | 54.7 | 51.6 | 68.8 | 222.4 | 214.9 | 214.9 | YES
3 | OK | 9 | 28 | 47 | 23 | 14 | 10.06 | 50 | 79.1 | 54.7 | 55.8 | 66.6 | 222.3 | 215.2 | 215.2 | YES
4 | OK | 28 | 13 | 47 | 23 | 14 | 6.37 | 50 | 79.1 | 54.7 | 64.3 | 62.1 | 221.1 | 217.9 | 217.9 | YES
5 | OK | 13 | 12 | 47 | 23 | 14 | 5.87 | 50 | 79.1 | 54.7 | 65.4 | 61.5 | 220.9 | 217.9 | 217.9 | YES
6 | OK | 12 | 27 | 47 | 23 | 14 | 5.05 | 50 | 79.1 | 54.7 | 67.3 | 60.6 | 220.9 | 217.9 | 217.9 | YES
7 | OK | 27 | 17 | 47 | 23 | 14 | 4.64 | 50 | 79.1 | 54.7 | 68.3 | 60.1 | 220.9 | 218 | 218 | YES
8 | OK | 17 | 11 | 47 | 23 | 14 | 4.64 | 50 | 79.1 | 54.7 | 68.3 | 60.1 | 220.9 | 218 | 218 | YES
9 | OK | 11 | 10 | 47 | 23 | 14 | 3.43 | 50 | 79.1 | 54.7 | 71.1 | 58.7 | 220.9 | 218.1 | 218.1 | YES
10 | ** OPTIMAL ** | 10 | 14 | 47 | 23 | 14 | 1.25 | 50 | 79.1 | 54.7 | 76.1 | 56.1 | 220 | 218.2 | 218.2 | YES
11 | OK | 14 | 46 | 47 | 23 | 14 | 1.25 | 50 | 79.1 | 54.7 | 76.1 | 56.1 | 220 | 218.2 | 218.2 | YES
12 | OK | 46 | 47 | 47 | 23 | 14 | 0.91 | 50 | 79.1 | 54.7 | 76.9 | 55.7 | 219.4 | 218.2 | 218.2 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 66-012726
TR_B (available) | 68-019290
TR_A Rated kVA | 50
TR_B Rated kVA | 100
TR_A Baseline Loading% | 79.1
TR_B Baseline Loading% | 54.7
Total Scenarios Evaluated | 16
Feasible Scenarios | 12
--- Optimal Solution ---
Switch Parent Node | 10
Switch Child Node | 14
Tie Node (TR_A side) | 47
Tie Node (TR_B side) | 23
Tie Line Distance (m) | 14
Load Transferred (kW) | 1.25
TR_A Loading After (%) | 76.1
TR_B Loading After (%) | 56.1
Minimum Voltage (V) | 218.2