## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 55 | 56 | 76 | 33 | 46.3 | 49.97 | 95 | 53.3 | 42.4 | 30.1 | 79.9 | 221.2 | 213.9 | 213.9 | YES
2 | OK | 56 | 42 | 76 | 33 | 46.3 | 49.96 | 95 | 53.3 | 42.4 | 30.1 | 79.9 | 221.1 | 213.9 | 213.9 | YES
3 | OK | 4 | 18 | 18 | 34 | 112.1 | 22.65 | 50 | 53.3 | 42.4 | 42.8 | 59.6 | 220.4 | 210.8 | 210.8 | YES
| NG | 4 | 3 | 3 | 34 | 130.6 | 40.81 | 95 | 53.3 | 42.4 | 34.2 | 74 | 222.2 | 208.3 | 208.3 | NO
4 | OK | 42 | 9 | 76 | 33 | 46.3 | 45.55 | 95 | 53.3 | 42.4 | 32.1 | 75.6 | 221 | 214.8 | 214.8 | YES
5 | OK | 18 | 19 | 19 | 34 | 117 | 22.46 | 50 | 53.3 | 42.4 | 42.9 | 59.4 | 220.4 | 210.9 | 210.9 | YES
6 | OK | 9 | 24 | 76 | 33 | 46.3 | 41.62 | 95 | 53.3 | 42.4 | 33.9 | 73.5 | 220.8 | 214.6 | 214.6 | YES
7 | OK | 9 | 10 | 10 | 34 | 145.2 | 1.24 | 50 | 53.3 | 42.4 | 52.8 | 43.3 | 219.9 | 220.5 | 219.9 | YES
8 | OK | 19 | 21 | 21 | 34 | 122 | 22.24 | 50 | 53.3 | 42.4 | 43 | 59.2 | 220.4 | 211 | 211 | YES
9 | OK | 24 | 11 | 76 | 33 | 46.3 | 41.62 | 95 | 53.3 | 42.4 | 33.9 | 72.1 | 220.8 | 215.6 | 215.6 | YES
10 | OK | 21 | 20 | 20 | 34 | 128.3 | 21.36 | 50 | 53.3 | 42.4 | 43.4 | 58.6 | 220.3 | 211 | 211 | YES
11 | OK | 11 | 12 | 76 | 33 | 46.3 | 36.56 | 95 | 53.3 | 42.4 | 36.2 | 69.7 | 220.7 | 216.2 | 216.2 | YES
12 | OK | 11 | 13 | 14 | 34 | 51.4 | 2.99 | 50 | 53.3 | 42.4 | 51.8 | 44.6 | 219.9 | 219.8 | 219.8 | YES
13 | OK | 20 | 23 | 23 | 34 | 143.6 | 19.96 | 50 | 53.3 | 42.4 | 44.1 | 57.5 | 220.2 | 210.8 | 210.8 | YES
14 | OK | 12 | 40 | 40 | 34 | 96.9 | 14.26 | 50 | 53.3 | 42.4 | 46.6 | 52.9 | 220.3 | 219.6 | 219.6 | YES
15 | OK | 12 | 41 | 76 | 33 | 46.3 | 22.3 | 95 | 53.3 | 42.4 | 42.9 | 58.9 | 220.3 | 216.9 | 216.9 | YES
16 | OK | 13 | 14 | 14 | 34 | 51.4 | 1.87 | 50 | 53.3 | 42.4 | 52.5 | 42.4 | 219.8 | 220.4 | 219.8 | YES
17 | OK | 40 | 60 | 60 | 34 | 116.9 | 13.76 | 50 | 53.3 | 42.4 | 46.9 | 52.6 | 220.3 | 219.9 | 219.9 | YES
18 | OK | 41 | 76 | 76 | 33 | 46.3 | 21.01 | 95 | 53.3 | 42.4 | 43.4 | 58 | 220.2 | 216.8 | 216.8 | YES
19 | OK | 60 | 66 | 66 | 34 | 141 | 7.91 | 50 | 53.3 | 42.4 | 49.6 | 48.2 | 220 | 220 | 220 | YES
20 | OK | 76 | 26 | 79 | 4 | 46.7 | 21.01 | 95 | 53.3 | 42.4 | 43.4 | 57.6 | 220.2 | 218.6 | 218.6 | YES
21 | OK | 66 | 61 | 61 | 34 | 144.6 | 7.91 | 50 | 53.3 | 42.4 | 49.6 | 47.2 | 220 | 219.8 | 219.8 | YES
22 | OK | 26 | 27 | 79 | 4 | 46.7 | 20.43 | 95 | 53.3 | 42.4 | 43.7 | 57.2 | 220.2 | 218.8 | 218.8 | YES
23 | OK | 27 | 89 | 79 | 4 | 46.7 | 20.43 | 95 | 53.3 | 42.4 | 43.7 | 57.2 | 220.2 | 218.8 | 218.8 | YES
24 | OK | 89 | 92 | 79 | 4 | 46.7 | 20.43 | 95 | 53.3 | 42.4 | 43.7 | 57.2 | 220.2 | 218.8 | 218.8 | YES
25 | OK | 92 | 93 | 79 | 4 | 46.7 | 20.43 | 95 | 53.3 | 42.4 | 43.7 | 57.2 | 220.2 | 218.8 | 218.8 | YES
26 | OK | 93 | 79 | 79 | 4 | 46.7 | 19.78 | 95 | 53.3 | 42.4 | 44 | 56.7 | 220.2 | 218.8 | 218.8 | YES
27 | OK | 79 | 80 | 80 | 60 | 47 | 6.79 | 95 | 53.3 | 42.4 | 49.8 | 47.3 | 219.8 | 219.2 | 219.2 | YES
28 | OK | 79 | 94 | 94 | 4 | 63.4 | 12.33 | 95 | 53.3 | 42.4 | 47.5 | 51.3 | 220.2 | 220 | 220 | YES
29 | OK | 80 | 77 | 74 | 52 | 47.7 | 6.42 | 95 | 53.3 | 42.4 | 50.3 | 47 | 219.8 | 219.6 | 219.6 | YES
30 | OK | 94 | 95 | 95 | 4 | 70 | 12.33 | 95 | 53.3 | 42.4 | 47.5 | 51.1 | 220.2 | 220 | 220 | YES
31 | OK | 77 | 78 | 74 | 52 | 47.7 | 6.42 | 95 | 53.3 | 42.4 | 50.3 | 47 | 219.8 | 219.6 | 219.6 | YES
32 | ** OPTIMAL ** | 95 | 90 | 90 | 4 | 105.1 | 11.58 | 95 | 53.3 | 42.4 | 47.9 | 50.8 | 220.2 | 220.1 | 220.1 | YES
33 | OK | 78 | 73 | 74 | 52 | 47.7 | 6.42 | 95 | 53.3 | 42.4 | 50.3 | 47 | 219.8 | 219.6 | 219.6 | YES
34 | OK | 90 | 91 | 91 | 4 | 129.5 | 9.54 | 95 | 53.3 | 42.4 | 48.8 | 49.3 | 220 | 220.1 | 220 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 66-016752
TR_B (available) | 41-005564
TR_A Rated kVA | 250
TR_B Rated kVA | 160
TR_A Baseline Loading% | 53.3
TR_B Baseline Loading% | 42.4
Total Scenarios Evaluated | 35
Feasible Scenarios | 34
--- Optimal Solution ---
Switch Parent Node | 95
Switch Child Node | 90
Tie Node (TR_A side) | 90
Tie Node (TR_B side) | 4
Tie Line Distance (m) | 105.1
Load Transferred (kW) | 11.58
TR_A Loading After (%) | 47.9
TR_B Loading After (%) | 50.8
Minimum Voltage (V) | 220.1