## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 55 | 5 | 8 | 20 | 5.7 | 64.53 | 50 | 53.3 | 11.7 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 55 | 56 | 69 | 11 | 73.5 | 49.97 | 50 | 53.3 | 11.7 | 30.1 | 52.2 | 221.2 | 194.2 | 194.2 | NO
| NG | 5 | 4 | 8 | 20 | 5.7 | 63.61 | 50 | 53.3 | 11.7 | 23.7 | 63.6 | 222.9 | 189 | 189 | NO
| NG | 56 | 42 | 69 | 11 | 73.5 | 49.96 | 50 | 53.3 | 11.7 | 30.1 | 52.2 | 221.1 | 194.2 | 194.2 | NO
1 | OK | 4 | 18 | 8 | 20 | 5.7 | 22.65 | 50 | 53.3 | 11.7 | 42.8 | 28.4 | 220.4 | 219 | 219 | YES
| NG | 42 | 9 | 69 | 11 | 73.5 | 45.55 | 50 | 53.3 | 11.7 | 32.1 | 47.1 | 221 | 198.4 | 198.4 | NO
2 | OK | 18 | 19 | 8 | 20 | 5.7 | 22.46 | 50 | 53.3 | 11.7 | 42.9 | 28.3 | 220.4 | 218.9 | 218.9 | YES
| NG | 9 | 24 | 69 | 11 | 73.5 | 41.62 | 50 | 53.3 | 11.7 | 33.9 | 44.7 | 220.8 | 197.3 | 197.3 | NO
3 | OK | 9 | 10 | 10 | 11 | 118.8 | 1.24 | 50 | 53.3 | 11.7 | 52.8 | 12.6 | 219.9 | 227.5 | 219.9 | YES
4 | OK | 19 | 21 | 8 | 20 | 5.7 | 22.24 | 50 | 53.3 | 11.7 | 43 | 28.1 | 220.4 | 218.9 | 218.9 | YES
| NG | 24 | 11 | 69 | 11 | 73.5 | 41.62 | 50 | 53.3 | 11.7 | 33.9 | 43.1 | 220.8 | 201.8 | 201.8 | NO
5 | OK | 21 | 20 | 8 | 20 | 5.7 | 21.36 | 50 | 53.3 | 11.7 | 43.4 | 27.4 | 220.3 | 218.7 | 218.7 | YES
| NG | 11 | 12 | 69 | 11 | 73.5 | 36.56 | 50 | 53.3 | 11.7 | 36.2 | 40.3 | 220.7 | 204.4 | 204.4 | NO
6 | OK | 20 | 23 | 8 | 20 | 5.7 | 19.96 | 50 | 53.3 | 11.7 | 44.1 | 26.4 | 220.2 | 218.3 | 218.3 | YES
7 | OK | 12 | 40 | 69 | 11 | 73.5 | 14.26 | 50 | 53.3 | 11.7 | 46.6 | 22.2 | 220.3 | 221.5 | 220.3 | YES
8 | OK | 12 | 41 | 86 | 11 | 127.8 | 22.3 | 50 | 53.3 | 11.7 | 42.9 | 28.7 | 220.3 | 210.8 | 210.8 | YES
9 | OK | 23 | 22 | 8 | 20 | 5.7 | 17.67 | 50 | 53.3 | 11.7 | 45.1 | 24.7 | 220.2 | 218 | 218 | YES
10 | ** OPTIMAL ** | 40 | 60 | 69 | 11 | 73.5 | 13.76 | 50 | 53.3 | 11.7 | 46.9 | 21.9 | 220.3 | 221.5 | 220.3 | YES
11 | OK | 41 | 76 | 86 | 11 | 127.8 | 21.01 | 50 | 53.3 | 11.7 | 43.4 | 27.7 | 220.2 | 210.4 | 210.4 | YES
12 | OK | 22 | 35 | 8 | 20 | 5.7 | 16.11 | 50 | 53.3 | 11.7 | 45.8 | 23.6 | 220 | 217.6 | 217.6 | YES
13 | OK | 60 | 66 | 69 | 11 | 73.5 | 7.91 | 50 | 53.3 | 11.7 | 49.6 | 17.5 | 220 | 226.1 | 220 | YES
14 | OK | 76 | 26 | 86 | 11 | 127.8 | 21.01 | 50 | 53.3 | 11.7 | 43.4 | 27.7 | 220.2 | 210.4 | 210.4 | YES
15 | OK | 35 | 34 | 34 | 11 | 106.2 | 6.04 | 50 | 53.3 | 11.7 | 50.5 | 16.3 | 219.8 | 219.6 | 219.6 | YES
16 | OK | 35 | 72 | 8 | 20 | 5.7 | 10.07 | 50 | 53.3 | 11.7 | 48.6 | 19 | 220 | 226.5 | 220 | YES
17 | OK | 66 | 61 | 69 | 11 | 73.5 | 7.91 | 50 | 53.3 | 11.7 | 49.6 | 16.5 | 220 | 225.9 | 220 | YES
18 | OK | 26 | 27 | 86 | 11 | 127.8 | 20.43 | 50 | 53.3 | 11.7 | 43.7 | 27.2 | 220.2 | 211.7 | 211.7 | YES
19 | OK | 72 | 37 | 8 | 20 | 5.7 | 8.34 | 50 | 53.3 | 11.7 | 49 | 17.8 | 220 | 226.5 | 220 | YES
20 | OK | 61 | 62 | 69 | 11 | 73.5 | 6.57 | 50 | 53.3 | 11.7 | 50.2 | 16.5 | 219.9 | 225.9 | 219.9 | YES
21 | OK | 27 | 89 | 86 | 11 | 127.8 | 20.43 | 50 | 53.3 | 11.7 | 43.7 | 27.2 | 220.2 | 211.7 | 211.7 | YES
22 | OK | 37 | 36 | 8 | 20 | 5.7 | 6.26 | 50 | 53.3 | 11.7 | 50.4 | 16.2 | 219.9 | 226.7 | 219.9 | YES
23 | OK | 62 | 67 | 69 | 11 | 73.5 | 3.49 | 50 | 53.3 | 11.7 | 50.2 | 14.3 | 219.9 | 225.6 | 219.9 | YES
24 | OK | 89 | 92 | 86 | 11 | 127.8 | 20.43 | 50 | 53.3 | 11.7 | 43.7 | 27.2 | 220.2 | 211.7 | 211.7 | YES
25 | OK | 36 | 54 | 8 | 20 | 5.7 | 4.2 | 50 | 53.3 | 11.7 | 51.4 | 14.8 | 219.9 | 227.1 | 219.9 | YES
26 | OK | 67 | 68 | 69 | 11 | 73.5 | 2.13 | 50 | 53.3 | 11.7 | 52.3 | 13.3 | 219.9 | 227.5 | 219.9 | YES
27 | OK | 92 | 93 | 88 | 11 | 130.1 | 20.43 | 50 | 53.3 | 11.7 | 43.7 | 27.1 | 220.2 | 211.5 | 211.5 | YES
28 | OK | 54 | 53 | 8 | 20 | 5.7 | 4.2 | 50 | 53.3 | 11.7 | 51.4 | 14.8 | 219.9 | 227.1 | 219.9 | YES
29 | OK | 68 | 63 | 69 | 11 | 73.5 | 2.13 | 50 | 53.3 | 11.7 | 52.3 | 13.3 | 219.9 | 227.5 | 219.9 | YES
30 | OK | 93 | 79 | 88 | 11 | 130.1 | 19.78 | 50 | 53.3 | 11.7 | 44 | 26.6 | 220.2 | 211.5 | 211.5 | YES
31 | OK | 53 | 39 | 8 | 20 | 5.7 | 4.2 | 50 | 53.3 | 11.7 | 51.4 | 14.8 | 219.9 | 227.1 | 219.9 | YES
32 | OK | 63 | 57 | 69 | 11 | 73.5 | 0.62 | 50 | 53.3 | 11.7 | 53 | 12.2 | 219.8 | 227.3 | 219.8 | YES
33 | OK | 79 | 94 | 88 | 11 | 130.1 | 12.33 | 50 | 53.3 | 11.7 | 47.5 | 20.8 | 220.2 | 223.6 | 220.2 | YES
34 | OK | 39 | 38 | 8 | 20 | 5.7 | 3.21 | 50 | 53.3 | 11.7 | 51.8 | 14 | 219.9 | 227.2 | 219.9 | YES
35 | OK | 57 | 58 | 69 | 11 | 73.5 | 0.6 | 50 | 53.3 | 11.7 | 53.1 | 12.2 | 219.8 | 227.3 | 219.8 | YES
36 | OK | 94 | 95 | 88 | 11 | 130.1 | 12.33 | 50 | 53.3 | 11.7 | 47.5 | 20.6 | 220.2 | 223.7 | 220.2 | YES
37 | OK | 38 | 25 | 8 | 20 | 5.7 | 1.83 | 50 | 53.3 | 11.7 | 52.5 | 13.1 | 219.8 | 227.2 | 219.8 | YES
38 | OK | 95 | 90 | 88 | 11 | 130.1 | 11.58 | 50 | 53.3 | 11.7 | 47.9 | 20.2 | 220.2 | 223.6 | 220.2 | YES
39 | OK | 25 | 6 | 8 | 20 | 5.7 | 1.8 | 50 | 53.3 | 11.7 | 52.5 | 13 | 219.8 | 227.2 | 219.8 | YES
40 | OK | 90 | 91 | 88 | 11 | 130.1 | 9.54 | 50 | 53.3 | 11.7 | 48.8 | 18.7 | 220 | 223.4 | 220 | YES
41 | OK | 6 | 7 | 8 | 20 | 5.7 | 1.8 | 50 | 53.3 | 11.7 | 52.5 | 13 | 219.8 | 227.2 | 219.8 | YES
42 | OK | 91 | 83 | 88 | 11 | 130.1 | 8.84 | 50 | 53.3 | 11.7 | 49.1 | 18.2 | 219.9 | 223.3 | 219.9 | YES
43 | OK | 7 | 8 | 8 | 20 | 5.7 | 1.61 | 50 | 53.3 | 11.7 | 52.6 | 11.7 | 219.8 | 227.3 | 219.8 | YES
44 | OK | 83 | 84 | 88 | 11 | 130.1 | 5.04 | 50 | 53.3 | 11.7 | 50.9 | 15.4 | 219.9 | 226 | 219.9 | YES
45 | OK | 84 | 87 | 88 | 11 | 130.1 | 4.93 | 50 | 53.3 | 11.7 | 51 | 15.3 | 219.9 | 226 | 219.9 | YES
46 | OK | 87 | 88 | 88 | 11 | 130.1 | 1.56 | 50 | 53.3 | 11.7 | 52.6 | 12.9 | 219.8 | 227.4 | 219.8 | YES
47 | OK | 88 | 81 | 81 | 11 | 134.4 | 1.56 | 50 | 53.3 | 11.7 | 52.6 | 12.9 | 219.8 | 227.4 | 219.8 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 66-016752
TR_B (available) | 49-003981
TR_A Rated kVA | 250
TR_B Rated kVA | 160
TR_A Baseline Loading% | 53.3
TR_B Baseline Loading% | 11.7
Total Scenarios Evaluated | 55
Feasible Scenarios | 47
--- Optimal Solution ---
Switch Parent Node | 40
Switch Child Node | 60
Tie Node (TR_A side) | 69
Tie Node (TR_B side) | 11
Tie Line Distance (m) | 73.5
Load Transferred (kW) | 13.76
TR_A Loading After (%) | 46.9
TR_B Loading After (%) | 21.9
Minimum Voltage (V) | 220.3