## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 28 | 0 | 65 | 1 | 97.8 | 32.1 | 50 | 53.3 | 15 | 38.2 | 86.4 | 222 | 210 | 210 | NO
1 | OK | 0 | 59 | 65 | 1 | 97.8 | 19.11 | 50 | 53.3 | 15 | 44.3 | 60.2 | 221.6 | 213.4 | 213.4 | YES
2 | ** OPTIMAL ** | 59 | 45 | 65 | 1 | 97.8 | 13.9 | 50 | 53.3 | 15 | 46.7 | 47.4 | 221.5 | 221.9 | 221.5 | YES
3 | OK | 45 | 46 | 65 | 1 | 97.8 | 10.12 | 50 | 53.3 | 15 | 47.6 | 37.5 | 221.4 | 223.2 | 221.4 | YES
4 | OK | 46 | 47 | 65 | 1 | 97.8 | 9.39 | 50 | 53.3 | 15 | 48.9 | 36.3 | 221.3 | 223.5 | 221.3 | YES
5 | OK | 47 | 43 | 65 | 1 | 97.8 | 6.69 | 50 | 53.3 | 15 | 49.1 | 30.6 | 221.3 | 223.2 | 221.3 | YES
6 | OK | 43 | 44 | 65 | 1 | 97.8 | 4.66 | 50 | 53.3 | 15 | 51.1 | 25.8 | 220.2 | 224.5 | 220.2 | YES
7 | OK | 44 | 64 | 65 | 1 | 97.8 | 2.25 | 50 | 53.3 | 15 | 52.3 | 20.2 | 220.8 | 227.7 | 220.8 | YES
8 | OK | 64 | 65 | 65 | 1 | 97.8 | 2.25 | 50 | 53.3 | 15 | 52.3 | 20.2 | 220.8 | 227.7 | 220.8 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 66-016752
TR_B (available) | 56-009275
TR_A Rated kVA | 250
TR_B Rated kVA | 50
TR_A Baseline Loading% | 53.3
TR_B Baseline Loading% | 15
Total Scenarios Evaluated | 9
Feasible Scenarios | 8
--- Optimal Solution ---
Switch Parent Node | 59
Switch Child Node | 45
Tie Node (TR_A side) | 65
Tie Node (TR_B side) | 1
Tie Line Distance (m) | 97.8
Load Transferred (kW) | 13.9
TR_A Loading After (%) | 46.7
TR_B Loading After (%) | 47.4
Minimum Voltage (V) | 221.5