## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 55 | 5 | 52 | 17 | 1.1 | 64.53 | 50 | 53.3 | 23.9 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 5 | 4 | 52 | 17 | 1.1 | 63.61 | 50 | 53.3 | 23.9 | 23.7 | 53 | 222.9 | 214.6 | 214.6 | YES
2 | OK | 4 | 18 | 37 | 72 | 107.7 | 22.65 | 50 | 53.3 | 23.9 | 42.8 | 27.7 | 220.4 | 218.4 | 218.4 | YES
3 | OK | 4 | 3 | 52 | 17 | 1.1 | 40.81 | 50 | 53.3 | 23.9 | 34.2 | 42.9 | 222.2 | 220.7 | 220.7 | YES
4 | OK | 18 | 19 | 37 | 72 | 107.7 | 22.46 | 50 | 53.3 | 23.9 | 42.9 | 27.7 | 220.4 | 218.4 | 218.4 | YES
5 | OK | 3 | 2 | 52 | 17 | 1.1 | 37.92 | 50 | 53.3 | 23.9 | 35.5 | 41.5 | 222.2 | 220.8 | 220.8 | YES
6 | OK | 19 | 21 | 37 | 72 | 107.7 | 22.24 | 50 | 53.3 | 23.9 | 43 | 27.7 | 220.4 | 218.4 | 218.4 | YES
7 | OK | 2 | 31 | 52 | 17 | 1.1 | 37.71 | 50 | 53.3 | 23.9 | 35.6 | 41.4 | 222.2 | 220.8 | 220.8 | YES
8 | OK | 21 | 20 | 37 | 72 | 107.7 | 21.36 | 50 | 53.3 | 23.9 | 43.4 | 27.7 | 220.3 | 218.4 | 218.4 | YES
9 | OK | 31 | 30 | 52 | 17 | 1.1 | 34.84 | 50 | 53.3 | 23.9 | 36.9 | 40.1 | 222.1 | 220.9 | 220.9 | YES
10 | OK | 31 | 32 | 33 | 15 | 105.4 | 1.97 | 50 | 53.3 | 23.9 | 52 | 24.8 | 220 | 221.9 | 220 | YES
11 | OK | 20 | 23 | 37 | 72 | 107.7 | 19.96 | 50 | 53.3 | 23.9 | 44.1 | 27.7 | 220.2 | 218.4 | 218.4 | YES
12 | OK | 30 | 71 | 52 | 17 | 1.1 | 34.35 | 50 | 53.3 | 23.9 | 37.2 | 39.9 | 222.1 | 220.9 | 220.9 | YES
13 | OK | 32 | 33 | 33 | 15 | 105.4 | 0.93 | 50 | 53.3 | 23.9 | 52.9 | 23.9 | 219.8 | 222 | 219.8 | YES
14 | OK | 23 | 22 | 37 | 72 | 107.7 | 17.67 | 50 | 53.3 | 23.9 | 45.1 | 27.7 | 220.2 | 218.4 | 218.4 | YES
15 | OK | 71 | 29 | 52 | 17 | 1.1 | 34.35 | 50 | 53.3 | 23.9 | 37.2 | 39.9 | 222.1 | 220.9 | 220.9 | YES
16 | OK | 22 | 35 | 37 | 72 | 107.7 | 16.11 | 50 | 53.3 | 23.9 | 45.8 | 27.7 | 220 | 218.4 | 218.4 | YES
17 | OK | 29 | 28 | 52 | 17 | 1.1 | 33.06 | 50 | 53.3 | 23.9 | 37.8 | 38.1 | 222.1 | 221 | 221 | YES
18 | OK | 35 | 34 | 34 | 72 | 142.2 | 6.04 | 50 | 53.3 | 23.9 | 50.5 | 26.8 | 219.8 | 220.8 | 219.8 | YES
19 | OK | 35 | 72 | 37 | 72 | 107.7 | 10.07 | 50 | 53.3 | 23.9 | 48.6 | 24.8 | 220 | 221.8 | 220 | YES
20 | OK | 28 | 0 | 52 | 17 | 1.1 | 32.1 | 50 | 53.3 | 23.9 | 38.2 | 37.7 | 222 | 221 | 221 | YES
21 | OK | 72 | 37 | 37 | 72 | 107.7 | 8.34 | 50 | 53.3 | 23.9 | 49 | 24.8 | 220 | 221.8 | 220 | YES
22 | OK | 0 | 1 | 52 | 17 | 1.1 | 9.3 | 50 | 53.3 | 23.9 | 48.9 | 28.1 | 220.5 | 221.6 | 220.5 | YES
23 | OK | 0 | 16 | 16 | 17 | 15.6 | 3.69 | 50 | 53.3 | 23.9 | 51.5 | 24.4 | 220.4 | 221.8 | 220.4 | YES
24 | ** OPTIMAL ** | 0 | 59 | 59 | 17 | 36.3 | 19.11 | 50 | 53.3 | 23.9 | 44.3 | 32.7 | 221.6 | 221.5 | 221.5 | YES
25 | OK | 37 | 36 | 36 | 72 | 112.2 | 6.26 | 50 | 53.3 | 23.9 | 50.4 | 24.4 | 219.9 | 221.9 | 219.9 | YES
26 | OK | 1 | 52 | 52 | 17 | 1.1 | 9.3 | 50 | 53.3 | 23.9 | 48.9 | 28.1 | 220.5 | 221.6 | 220.5 | YES
27 | OK | 16 | 17 | 17 | 17 | 27.2 | 3.69 | 50 | 53.3 | 23.9 | 51.6 | 23.9 | 220.2 | 222 | 220.2 | YES
28 | OK | 59 | 45 | 45 | 17 | 48.6 | 13.9 | 50 | 53.3 | 23.9 | 46.7 | 30.3 | 221.5 | 221.4 | 221.4 | YES
29 | OK | 36 | 54 | 54 | 72 | 124.1 | 4.2 | 50 | 53.3 | 23.9 | 51.4 | 24.3 | 219.9 | 221.9 | 219.9 | YES
30 | OK | 52 | 48 | 48 | 71 | 25.4 | 9.12 | 50 | 53.3 | 23.9 | 49 | 28.1 | 220.4 | 221.3 | 220.4 | YES
31 | OK | 45 | 46 | 46 | 17 | 58.3 | 10.12 | 50 | 53.3 | 23.9 | 47.6 | 28.4 | 221.4 | 221.4 | 221.4 | YES
32 | OK | 45 | 70 | 70 | 17 | 61 | 2.82 | 50 | 53.3 | 23.9 | 52 | 24.3 | 220.3 | 222 | 220.3 | YES
33 | OK | 54 | 53 | 53 | 72 | 125.1 | 4.2 | 50 | 53.3 | 23.9 | 51.4 | 24.3 | 219.9 | 221.9 | 219.9 | YES
34 | OK | 48 | 49 | 51 | 34 | 47.2 | 6.59 | 50 | 53.3 | 23.9 | 50.2 | 27 | 220.8 | 218.4 | 218.4 | YES
35 | OK | 46 | 47 | 47 | 17 | 66.4 | 9.39 | 50 | 53.3 | 23.9 | 48.9 | 28.1 | 221.3 | 221.4 | 221.3 | YES
36 | OK | 53 | 39 | 39 | 72 | 126.3 | 4.2 | 50 | 53.3 | 23.9 | 51.4 | 24.3 | 219.9 | 221.9 | 219.9 | YES
37 | OK | 49 | 50 | 51 | 34 | 47.2 | 5.82 | 50 | 53.3 | 23.9 | 50.6 | 26.7 | 220.7 | 218.2 | 218.2 | YES
38 | OK | 47 | 43 | 43 | 17 | 72.4 | 6.69 | 50 | 53.3 | 23.9 | 49.1 | 27 | 221.3 | 221.4 | 221.3 | YES
39 | OK | 50 | 51 | 51 | 34 | 47.2 | 3.39 | 50 | 53.3 | 23.9 | 51.7 | 25.5 | 219.7 | 217.6 | 217.6 | YES
40 | OK | 43 | 44 | 44 | 17 | 74.5 | 4.66 | 50 | 53.3 | 23.9 | 51.1 | 26 | 220.2 | 221.5 | 220.2 | YES
41 | OK | 44 | 64 | 64 | 17 | 119.6 | 2.25 | 50 | 53.3 | 23.9 | 52.3 | 24.9 | 220.8 | 221.9 | 220.8 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 66-016752
TR_B (available) | 60-039913
TR_A Rated kVA | 250
TR_B Rated kVA | 250
TR_A Baseline Loading% | 53.3
TR_B Baseline Loading% | 23.9
Total Scenarios Evaluated | 42
Feasible Scenarios | 41
--- Optimal Solution ---
Switch Parent Node | 0
Switch Child Node | 59
Tie Node (TR_A side) | 59
Tie Node (TR_B side) | 17
Tie Line Distance (m) | 36.3
Load Transferred (kW) | 19.11
TR_A Loading After (%) | 44.3
TR_B Loading After (%) | 32.7
Minimum Voltage (V) | 221.5