## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 55 | 5 | 8 | 17 | 60.8 | 64.53 | 50 | 53.3 | 36.2 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 55 | 56 | 69 | 21 | 2.2 | 49.97 | 50 | 53.3 | 36.2 | 30.1 | 75.8 | 221.2 | 200.5 | 200.5 | NO
| NG | 5 | 4 | 8 | 17 | 60.8 | 63.61 | 50 | 53.3 | 36.2 | 23.7 | 89.9 | 222.9 | 180.2 | 180.2 | NO
| NG | 56 | 42 | 69 | 21 | 2.2 | 49.96 | 50 | 53.3 | 36.2 | 30.1 | 75.8 | 221.1 | 200.5 | 200.5 | NO
1 | OK | 4 | 18 | 8 | 17 | 60.8 | 22.65 | 50 | 53.3 | 36.2 | 42.8 | 53 | 220.4 | 216.6 | 216.6 | YES
| NG | 42 | 9 | 69 | 21 | 2.2 | 45.55 | 50 | 53.3 | 36.2 | 32.1 | 71 | 221 | 201.5 | 201.5 | NO
2 | OK | 18 | 19 | 8 | 17 | 60.8 | 22.46 | 50 | 53.3 | 36.2 | 42.9 | 52.8 | 220.4 | 216.6 | 216.6 | YES
| NG | 9 | 24 | 69 | 21 | 2.2 | 41.62 | 50 | 53.3 | 36.2 | 33.9 | 68.6 | 220.8 | 203.1 | 203.1 | NO
3 | OK | 9 | 10 | 10 | 21 | 119.3 | 1.24 | 50 | 53.3 | 36.2 | 52.8 | 37.1 | 219.9 | 224.8 | 219.9 | YES
4 | OK | 19 | 21 | 8 | 17 | 60.8 | 22.24 | 50 | 53.3 | 36.2 | 43 | 52.6 | 220.4 | 216.5 | 216.5 | YES
| NG | 24 | 11 | 69 | 21 | 2.2 | 41.62 | 50 | 53.3 | 36.2 | 33.9 | 67.1 | 220.8 | 204.5 | 204.5 | NO
5 | OK | 21 | 20 | 8 | 17 | 60.8 | 21.36 | 50 | 53.3 | 36.2 | 43.4 | 52 | 220.3 | 216.3 | 216.3 | YES
| NG | 11 | 12 | 69 | 21 | 2.2 | 36.56 | 50 | 53.3 | 36.2 | 36.2 | 64.4 | 220.7 | 206 | 206 | NO
6 | OK | 20 | 23 | 8 | 17 | 60.8 | 19.96 | 50 | 53.3 | 36.2 | 44.1 | 50.9 | 220.2 | 215.8 | 215.8 | YES
7 | OK | 12 | 40 | 69 | 21 | 2.2 | 14.26 | 50 | 53.3 | 36.2 | 46.6 | 46.7 | 220.3 | 220.8 | 220.3 | YES
8 | OK | 12 | 41 | 88 | 24 | 51.9 | 22.3 | 50 | 53.3 | 36.2 | 42.9 | 52.9 | 220.3 | 214.3 | 214.3 | YES
9 | OK | 23 | 22 | 8 | 17 | 60.8 | 17.67 | 50 | 53.3 | 36.2 | 45.1 | 49.2 | 220.2 | 215.4 | 215.4 | YES
10 | ** OPTIMAL ** | 40 | 60 | 69 | 21 | 2.2 | 13.76 | 50 | 53.3 | 36.2 | 46.9 | 46.3 | 220.3 | 220.8 | 220.3 | YES
11 | OK | 41 | 76 | 88 | 24 | 51.9 | 21.01 | 50 | 53.3 | 36.2 | 43.4 | 51.9 | 220.2 | 213.9 | 213.9 | YES
12 | OK | 22 | 35 | 8 | 17 | 60.8 | 16.11 | 50 | 53.3 | 36.2 | 45.8 | 48.1 | 220 | 214.8 | 214.8 | YES
13 | OK | 60 | 66 | 69 | 21 | 2.2 | 7.91 | 50 | 53.3 | 36.2 | 49.6 | 41.9 | 220 | 223 | 220 | YES
14 | OK | 76 | 26 | 88 | 24 | 51.9 | 21.01 | 50 | 53.3 | 36.2 | 43.4 | 51.9 | 220.2 | 213.9 | 213.9 | YES
15 | OK | 35 | 34 | 34 | 21 | 116.8 | 6.04 | 50 | 53.3 | 36.2 | 50.5 | 40.6 | 219.8 | 220.3 | 219.8 | YES
16 | OK | 35 | 72 | 8 | 17 | 60.8 | 10.07 | 50 | 53.3 | 36.2 | 48.6 | 43.5 | 220 | 222.7 | 220 | YES
17 | OK | 66 | 61 | 69 | 21 | 2.2 | 7.91 | 50 | 53.3 | 36.2 | 49.6 | 41 | 220 | 222.9 | 220 | YES
18 | OK | 26 | 27 | 88 | 24 | 51.9 | 20.43 | 50 | 53.3 | 36.2 | 43.7 | 51.4 | 220.2 | 215.1 | 215.1 | YES
19 | OK | 72 | 37 | 8 | 17 | 60.8 | 8.34 | 50 | 53.3 | 36.2 | 49 | 42.2 | 220 | 224.3 | 220 | YES
20 | OK | 61 | 62 | 69 | 21 | 2.2 | 6.57 | 50 | 53.3 | 36.2 | 50.2 | 41 | 219.9 | 222.9 | 219.9 | YES
21 | OK | 27 | 89 | 88 | 24 | 51.9 | 20.43 | 50 | 53.3 | 36.2 | 43.7 | 51.4 | 220.2 | 215.1 | 215.1 | YES
22 | OK | 37 | 36 | 8 | 17 | 60.8 | 6.26 | 50 | 53.3 | 36.2 | 50.4 | 40.7 | 219.9 | 224.4 | 219.9 | YES
23 | OK | 62 | 67 | 69 | 21 | 2.2 | 3.49 | 50 | 53.3 | 36.2 | 50.2 | 38.7 | 219.9 | 224.7 | 219.9 | YES
24 | OK | 89 | 92 | 88 | 24 | 51.9 | 20.43 | 50 | 53.3 | 36.2 | 43.7 | 51.4 | 220.2 | 215.1 | 215.1 | YES
25 | OK | 36 | 54 | 8 | 17 | 60.8 | 4.2 | 50 | 53.3 | 36.2 | 51.4 | 39.2 | 219.9 | 224.5 | 219.9 | YES
26 | OK | 67 | 68 | 69 | 21 | 2.2 | 2.13 | 50 | 53.3 | 36.2 | 52.3 | 37.7 | 219.9 | 224.7 | 219.9 | YES
27 | OK | 92 | 93 | 88 | 24 | 51.9 | 20.43 | 50 | 53.3 | 36.2 | 43.7 | 51.4 | 220.2 | 215.1 | 215.1 | YES
28 | OK | 54 | 53 | 8 | 17 | 60.8 | 4.2 | 50 | 53.3 | 36.2 | 51.4 | 39.2 | 219.9 | 224.5 | 219.9 | YES
29 | OK | 68 | 63 | 69 | 21 | 2.2 | 2.13 | 50 | 53.3 | 36.2 | 52.3 | 37.7 | 219.9 | 224.7 | 219.9 | YES
30 | OK | 93 | 79 | 88 | 24 | 51.9 | 19.78 | 50 | 53.3 | 36.2 | 44 | 50.9 | 220.2 | 215.1 | 215.1 | YES
31 | OK | 53 | 39 | 8 | 17 | 60.8 | 4.2 | 50 | 53.3 | 36.2 | 51.4 | 39.2 | 219.9 | 224.5 | 219.9 | YES
32 | OK | 63 | 57 | 69 | 21 | 2.2 | 0.62 | 50 | 53.3 | 36.2 | 53 | 36.6 | 219.8 | 224.7 | 219.8 | YES
33 | OK | 79 | 94 | 88 | 24 | 51.9 | 12.33 | 50 | 53.3 | 36.2 | 47.5 | 45.2 | 220.2 | 221.1 | 220.2 | YES
34 | OK | 39 | 38 | 8 | 17 | 60.8 | 3.21 | 50 | 53.3 | 36.2 | 51.8 | 38.5 | 219.9 | 224.5 | 219.9 | YES
35 | OK | 57 | 58 | 69 | 21 | 2.2 | 0.6 | 50 | 53.3 | 36.2 | 53.1 | 36.6 | 219.8 | 224.7 | 219.8 | YES
36 | OK | 94 | 95 | 88 | 24 | 51.9 | 12.33 | 50 | 53.3 | 36.2 | 47.5 | 45 | 220.2 | 221.1 | 220.2 | YES
37 | OK | 38 | 25 | 8 | 17 | 60.8 | 1.83 | 50 | 53.3 | 36.2 | 52.5 | 37.5 | 219.8 | 224.6 | 219.8 | YES
38 | OK | 95 | 90 | 88 | 24 | 51.9 | 11.58 | 50 | 53.3 | 36.2 | 47.9 | 44.7 | 220.2 | 220.9 | 220.2 | YES
39 | OK | 25 | 6 | 8 | 17 | 60.8 | 1.8 | 50 | 53.3 | 36.2 | 52.5 | 37.5 | 219.8 | 224.6 | 219.8 | YES
40 | OK | 90 | 91 | 88 | 24 | 51.9 | 9.54 | 50 | 53.3 | 36.2 | 48.8 | 43.2 | 220 | 220.7 | 220 | YES
41 | OK | 6 | 7 | 8 | 17 | 60.8 | 1.8 | 50 | 53.3 | 36.2 | 52.5 | 37.5 | 219.8 | 224.6 | 219.8 | YES
42 | OK | 91 | 83 | 88 | 24 | 51.9 | 8.84 | 50 | 53.3 | 36.2 | 49.1 | 42.7 | 219.9 | 220.7 | 219.9 | YES
43 | OK | 7 | 8 | 8 | 17 | 60.8 | 1.61 | 50 | 53.3 | 36.2 | 52.6 | 36.2 | 219.8 | 224.8 | 219.8 | YES
44 | OK | 83 | 84 | 88 | 24 | 51.9 | 5.04 | 50 | 53.3 | 36.2 | 50.9 | 39.9 | 219.9 | 222.9 | 219.9 | YES
45 | OK | 84 | 87 | 88 | 24 | 51.9 | 4.93 | 50 | 53.3 | 36.2 | 51 | 39.8 | 219.9 | 222.9 | 219.9 | YES
46 | OK | 87 | 88 | 88 | 24 | 51.9 | 1.56 | 50 | 53.3 | 36.2 | 52.6 | 37.3 | 219.8 | 224.6 | 219.8 | YES
47 | OK | 88 | 81 | 81 | 24 | 56.2 | 1.56 | 50 | 53.3 | 36.2 | 52.6 | 37.3 | 219.8 | 224.6 | 219.8 | YES
48 | OK | 81 | 82 | 82 | 24 | 77.8 | 1.56 | 50 | 53.3 | 36.2 | 52.6 | 37.3 | 219.8 | 224.6 | 219.8 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 66-016752
TR_B (available) | 67-006111
TR_A Rated kVA | 250
TR_B Rated kVA | 160
TR_A Baseline Loading% | 53.3
TR_B Baseline Loading% | 36.2
Total Scenarios Evaluated | 56
Feasible Scenarios | 48
--- Optimal Solution ---
Switch Parent Node | 40
Switch Child Node | 60
Tie Node (TR_A side) | 69
Tie Node (TR_B side) | 21
Tie Line Distance (m) | 2.2
Load Transferred (kW) | 13.76
TR_A Loading After (%) | 46.9
TR_B Loading After (%) | 46.3
Minimum Voltage (V) | 220.3