## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 55 | 5 | 31 | 18 | 2 | 64.53 | 50 | 53.3 | 20.8 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 55 | 56 | 56 | 18 | 65.6 | 49.97 | 50 | 53.3 | 20.8 | 30.1 | 59.4 | 221.2 | 205.5 | 205.5 | NO
| NG | 5 | 4 | 31 | 18 | 2 | 63.61 | 50 | 53.3 | 20.8 | 23.7 | 69.4 | 222.9 | 207.9 | 207.9 | NO
| NG | 56 | 42 | 42 | 18 | 84.8 | 49.96 | 50 | 53.3 | 20.8 | 30.1 | 59.5 | 221.1 | 205.1 | 205.1 | NO
1 | OK | 4 | 18 | 54 | 21 | 40.3 | 22.65 | 50 | 53.3 | 20.8 | 42.8 | 37.3 | 220.4 | 219.6 | 219.6 | YES
2 | OK | 4 | 3 | 31 | 18 | 2 | 40.81 | 50 | 53.3 | 20.8 | 34.2 | 51.5 | 222.2 | 215.5 | 215.5 | YES
3 | OK | 42 | 9 | 10 | 2 | 96.6 | 45.55 | 50 | 53.3 | 20.8 | 32.1 | 31.4 | 221 | 213.1 | 213.1 | YES
4 | OK | 18 | 19 | 54 | 21 | 40.3 | 22.46 | 50 | 53.3 | 20.8 | 42.9 | 37.2 | 220.4 | 219.6 | 219.6 | YES
5 | OK | 3 | 2 | 31 | 18 | 2 | 37.92 | 50 | 53.3 | 20.8 | 35.5 | 49.3 | 222.2 | 215.9 | 215.9 | YES
| NG | 9 | 24 | 24 | 18 | 121 | 41.62 | 50 | 53.3 | 20.8 | 33.9 | 52.9 | 220.8 | 205.8 | 205.8 | NO
6 | OK | 9 | 10 | 10 | 2 | 96.6 | 1.24 | 50 | 53.3 | 20.8 | 52.8 | 21.7 | 219.9 | 225.6 | 219.9 | YES
7 | OK | 19 | 21 | 54 | 21 | 40.3 | 22.24 | 50 | 53.3 | 20.8 | 43 | 37 | 220.4 | 219.5 | 219.5 | YES
8 | OK | 2 | 31 | 31 | 18 | 2 | 37.71 | 50 | 53.3 | 20.8 | 35.6 | 49.1 | 222.2 | 215.9 | 215.9 | YES
| NG | 24 | 11 | 11 | 18 | 123.1 | 41.62 | 50 | 53.3 | 20.8 | 33.9 | 51.5 | 220.8 | 208.2 | 208.2 | NO
9 | OK | 21 | 20 | 54 | 21 | 40.3 | 21.36 | 50 | 53.3 | 20.8 | 43.4 | 36.4 | 220.3 | 219.4 | 219.4 | YES
10 | OK | 31 | 30 | 30 | 18 | 36.8 | 34.84 | 50 | 53.3 | 20.8 | 36.9 | 47 | 222.1 | 216.2 | 216.2 | YES
11 | OK | 31 | 32 | 32 | 18 | 8.3 | 1.97 | 50 | 53.3 | 20.8 | 52 | 22.2 | 220 | 225.3 | 220 | YES
| NG | 11 | 12 | 68 | 20 | 145.4 | 36.56 | 50 | 53.3 | 20.8 | 36.2 | 48.6 | 220.7 | 209.7 | 209.7 | NO
12 | OK | 11 | 13 | 13 | 18 | 127.6 | 2.99 | 50 | 53.3 | 20.8 | 51.8 | 22.9 | 219.9 | 224.6 | 219.9 | YES
13 | OK | 20 | 23 | 54 | 21 | 40.3 | 19.96 | 50 | 53.3 | 20.8 | 44.1 | 35.4 | 220.2 | 219.1 | 219.1 | YES
14 | OK | 30 | 71 | 71 | 18 | 52.3 | 34.35 | 50 | 53.3 | 20.8 | 37.2 | 46.6 | 222.1 | 215.9 | 215.9 | YES
15 | OK | 32 | 33 | 33 | 18 | 15.8 | 0.93 | 50 | 53.3 | 20.8 | 52.9 | 20.8 | 219.8 | 225.6 | 219.8 | YES
16 | OK | 12 | 40 | 68 | 20 | 145.4 | 14.26 | 50 | 53.3 | 20.8 | 46.6 | 31.2 | 220.3 | 224 | 220.3 | YES
17 | OK | 13 | 14 | 14 | 18 | 131.3 | 1.87 | 50 | 53.3 | 20.8 | 52.5 | 20.8 | 219.8 | 225.6 | 219.8 | YES
18 | OK | 23 | 22 | 54 | 21 | 40.3 | 17.67 | 50 | 53.3 | 20.8 | 45.1 | 33.7 | 220.2 | 218.9 | 218.9 | YES
19 | OK | 71 | 29 | 29 | 18 | 97.6 | 34.35 | 50 | 53.3 | 20.8 | 37.2 | 46.7 | 222.1 | 215.5 | 215.5 | YES
20 | OK | 40 | 60 | 68 | 20 | 145.4 | 13.76 | 50 | 53.3 | 20.8 | 46.9 | 30.8 | 220.3 | 224 | 220.3 | YES
21 | OK | 22 | 35 | 54 | 21 | 40.3 | 16.11 | 50 | 53.3 | 20.8 | 45.8 | 32.6 | 220 | 218.5 | 218.5 | YES
22 | OK | 29 | 28 | 17 | 18 | 100.4 | 33.06 | 50 | 53.3 | 20.8 | 37.8 | 43.8 | 222.1 | 216 | 216 | YES
23 | OK | 60 | 66 | 68 | 20 | 145.4 | 7.91 | 50 | 53.3 | 20.8 | 49.6 | 26.5 | 220 | 225.4 | 220 | YES
24 | OK | 35 | 34 | 34 | 2 | 87.1 | 6.04 | 50 | 53.3 | 20.8 | 50.5 | 25.2 | 219.8 | 222.7 | 219.8 | YES
25 | OK | 35 | 72 | 54 | 21 | 40.3 | 10.07 | 50 | 53.3 | 20.8 | 48.6 | 28 | 220 | 225.2 | 220 | YES
26 | OK | 28 | 0 | 17 | 18 | 100.4 | 32.1 | 50 | 53.3 | 20.8 | 38.2 | 43.1 | 222 | 216 | 216 | YES
27 | OK | 66 | 61 | 68 | 20 | 145.4 | 7.91 | 50 | 53.3 | 20.8 | 49.6 | 25.5 | 220 | 225.4 | 220 | YES
28 | OK | 72 | 37 | 54 | 21 | 40.3 | 8.34 | 50 | 53.3 | 20.8 | 49 | 26.8 | 220 | 225.2 | 220 | YES
29 | OK | 0 | 1 | 52 | 16 | 116.7 | 9.3 | 50 | 53.3 | 20.8 | 48.9 | 27.4 | 220.5 | 221.1 | 220.5 | YES
30 | OK | 0 | 16 | 17 | 18 | 100.4 | 3.69 | 50 | 53.3 | 20.8 | 51.5 | 21.7 | 220.4 | 224.4 | 220.4 | YES
31 | OK | 61 | 62 | 68 | 20 | 145.4 | 6.57 | 50 | 53.3 | 20.8 | 50.2 | 25.5 | 219.9 | 225.4 | 219.9 | YES
32 | OK | 37 | 36 | 54 | 21 | 40.3 | 6.26 | 50 | 53.3 | 20.8 | 50.4 | 25.3 | 219.9 | 225.3 | 219.9 | YES
33 | ** OPTIMAL ** | 1 | 52 | 52 | 16 | 116.7 | 9.3 | 50 | 53.3 | 20.8 | 48.9 | 27.4 | 220.5 | 221.1 | 220.5 | YES
34 | OK | 16 | 17 | 17 | 18 | 100.4 | 3.69 | 50 | 53.3 | 20.8 | 51.6 | 20.8 | 220.2 | 225.6 | 220.2 | YES
35 | OK | 62 | 67 | 68 | 20 | 145.4 | 3.49 | 50 | 53.3 | 20.8 | 50.2 | 23.3 | 219.9 | 225.4 | 219.9 | YES
36 | OK | 36 | 54 | 54 | 21 | 40.3 | 4.2 | 50 | 53.3 | 20.8 | 51.4 | 23.8 | 219.9 | 225.5 | 219.9 | YES
37 | OK | 52 | 48 | 48 | 16 | 136.7 | 9.12 | 50 | 53.3 | 20.8 | 49 | 27.4 | 220.4 | 221.2 | 220.4 | YES
38 | OK | 67 | 68 | 68 | 20 | 145.4 | 2.13 | 50 | 53.3 | 20.8 | 52.3 | 22.3 | 219.9 | 225.6 | 219.9 | YES
39 | OK | 54 | 53 | 53 | 21 | 40.9 | 4.2 | 50 | 53.3 | 20.8 | 51.4 | 23.8 | 219.9 | 225.5 | 219.9 | YES
40 | OK | 53 | 39 | 39 | 21 | 41.7 | 4.2 | 50 | 53.3 | 20.8 | 51.4 | 23.8 | 219.9 | 225.5 | 219.9 | YES
41 | OK | 39 | 38 | 15 | 0 | 45.9 | 3.21 | 50 | 53.3 | 20.8 | 51.8 | 23.1 | 219.9 | 225.5 | 219.9 | YES
42 | OK | 38 | 25 | 15 | 0 | 45.9 | 1.83 | 50 | 53.3 | 20.8 | 52.5 | 22.1 | 219.8 | 225.5 | 219.8 | YES
43 | OK | 25 | 6 | 15 | 0 | 45.9 | 1.8 | 50 | 53.3 | 20.8 | 52.5 | 22.1 | 219.8 | 225.5 | 219.8 | YES
44 | OK | 6 | 7 | 7 | 7 | 63.3 | 1.8 | 50 | 53.3 | 20.8 | 52.5 | 22.1 | 219.8 | 225.5 | 219.8 | YES
45 | OK | 7 | 8 | 8 | 7 | 74.6 | 1.61 | 50 | 53.3 | 20.8 | 52.6 | 20.8 | 219.8 | 225.6 | 219.8 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 66-016752
TR_B (available) | 67-038731
TR_A Rated kVA | 250
TR_B Rated kVA | 160
TR_A Baseline Loading% | 53.3
TR_B Baseline Loading% | 20.8
Total Scenarios Evaluated | 52
Feasible Scenarios | 45
--- Optimal Solution ---
Switch Parent Node | 1
Switch Child Node | 52
Tie Node (TR_A side) | 52
Tie Node (TR_B side) | 16
Tie Line Distance (m) | 116.7
Load Transferred (kW) | 9.3
TR_A Loading After (%) | 48.9
TR_B Loading After (%) | 27.4
Minimum Voltage (V) | 220.5