## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 64 | 29 | 25 | 43 | 88.2 | 9.19 | 50 | 17 | 14.4 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 64 | 52 | 23 | 43 | 4.7 | 49.2 | 50 | 17 | 14.4 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 29 | 30 | 25 | 43 | 88.2 | 7.86 | 50 | 17 | 14.4 | 13.6 | 20.3 | 48.8 | 220.1 | 48.8 | NO
1 | OK | 29 | 87 | 87 | 43 | 227 | 0.69 | 50 | 17 | 14.4 | 16.2 | 14.9 | 221 | 223.2 | 221 | YES
2 | OK | 29 | 21 | 21 | 43 | 217.4 | 0.64 | 50 | 17 | 14.4 | 17 | 14.9 | 220.8 | 223.3 | 220.8 | YES
3 | OK | 52 | 51 | 23 | 43 | 4.7 | 2.03 | 50 | 17 | 14.4 | 15.9 | 15.9 | 221 | 223.2 | 221 | YES
| NG | 52 | 53 | 53 | 43 | 60.6 | 47.17 | 50 | 17 | 14.4 | [5 empty] | NO | TR_B sim: not converged
4 | OK | 30 | 27 | 25 | 43 | 88.2 | 7.26 | 50 | 17 | 14.4 | 13.6 | 19.8 | 221.5 | 219.8 | 219.8 | YES
5 | OK | 21 | 20 | 20 | 43 | 219.3 | 0.64 | 50 | 17 | 14.4 | 17 | 14.9 | 220.8 | 223.3 | 220.8 | YES
6 | OK | 51 | 84 | 23 | 43 | 4.7 | 2.03 | 50 | 17 | 14.4 | 15.9 | 15.9 | 221 | 223.2 | 221 | YES
7 | OK | 53 | 54 | 54 | 43 | 97.5 | 4.66 | 50 | 17 | 14.4 | 15 | 17.8 | 219.4 | 223.1 | 219.4 | YES
| NG | 53 | 65 | 65 | 43 | 62.9 | 42.51 | 50 | 17 | 14.4 | 7.5 | 20.8 | 227.8 | 205.8 | 205.8 | NO
8 | OK | 27 | 28 | 25 | 43 | 88.2 | 6.09 | 50 | 17 | 14.4 | 13.6 | 19 | 221.5 | 219.3 | 219.3 | YES
9 | OK | 27 | 71 | 74 | 43 | 167.1 | 1.17 | 50 | 17 | 14.4 | 17 | 15.3 | 220.8 | 223.3 | 220.8 | YES
10 | OK | 84 | 22 | 23 | 43 | 4.7 | 2.03 | 50 | 17 | 14.4 | 15.9 | 15.9 | 221 | 223.2 | 221 | YES
11 | OK | 54 | 55 | 55 | 43 | 138.3 | 2.79 | 50 | 17 | 14.4 | 15 | 16.5 | 219.4 | 223.1 | 219.4 | YES
| NG | 65 | 62 | 62 | 43 | 176.8 | 42.42 | 50 | 17 | 14.4 | 7.5 | 20.9 | 227.7 | 205.5 | 205.5 | NO
12 | ** OPTIMAL ** | 28 | 88 | 89 | 43 | 146.3 | 1.37 | 50 | 17 | 14.4 | 15.4 | 15.4 | 221.1 | 223.1 | 221.1 | YES
13 | OK | 28 | 69 | 25 | 43 | 88.2 | 4.72 | 50 | 17 | 14.4 | 15.2 | 18 | 221.2 | 219.1 | 219.1 | YES
14 | OK | 71 | 74 | 74 | 43 | 167.1 | 0.47 | 50 | 17 | 14.4 | 17 | 14.8 | 220.8 | 223.3 | 220.8 | YES
15 | OK | 22 | 16 | 23 | 43 | 4.7 | 1.59 | 50 | 17 | 14.4 | 16.4 | 15.6 | 220.9 | 223.3 | 220.9 | YES
16 | OK | 55 | 56 | 56 | 43 | 160.4 | 2.79 | 50 | 17 | 14.4 | 15 | 16.5 | 219.4 | 223.1 | 219.4 | YES
| NG | 62 | 40 | 15 | 43 | 212 | 41.43 | 50 | 17 | 14.4 | 7.5 | 20.8 | 227.7 | 207.9 | 207.9 | NO
17 | OK | 69 | 70 | 25 | 43 | 88.2 | 2.61 | 50 | 17 | 14.4 | 17.1 | 16.4 | 220.8 | 219.9 | 219.9 | YES
18 | OK | 16 | 17 | 17 | 43 | 50.5 | 1.56 | 50 | 17 | 14.4 | 16.5 | 15.6 | 220.9 | 223.3 | 220.9 | YES
19 | OK | 16 | 23 | 23 | 43 | 4.7 | 0.03 | 50 | 17 | 14.4 | 17 | 14.5 | 220.8 | 223.3 | 220.8 | YES
20 | OK | 56 | 67 | 67 | 43 | 177.5 | 2.34 | 50 | 17 | 14.4 | 15.5 | 16.2 | 219.3 | 223.1 | 219.3 | YES
21 | OK | 40 | 7 | 66 | 43 | 234.2 | 9.95 | 50 | 17 | 14.4 | 10.2 | 17.7 | 226 | 214.7 | 214.7 | YES
22 | OK | 40 | 50 | 9 | 43 | 240.9 | 1.33 | 50 | 17 | 14.4 | 17.1 | 15.4 | 218.9 | 222 | 218.9 | YES
23 | OK | 40 | 15 | 15 | 43 | 212 | 0.38 | 50 | 17 | 14.4 | 16.6 | 14.7 | 221.1 | 223.3 | 221.1 | YES
24 | OK | 70 | 26 | 25 | 43 | 88.2 | 2.61 | 50 | 17 | 14.4 | 17.1 | 16.4 | 220.8 | 219.9 | 219.9 | YES
25 | OK | 17 | 24 | 24 | 43 | 83.4 | 0.14 | 50 | 17 | 14.4 | 17.1 | 14.5 | 220.8 | 223.3 | 220.8 | YES
26 | OK | 67 | 68 | 68 | 43 | 188.4 | 2.34 | 50 | 17 | 14.4 | 15.5 | 16.2 | 219.3 | 223.1 | 219.3 | YES
27 | OK | 7 | 6 | 66 | 43 | 234.2 | 9.95 | 50 | 17 | 14.4 | 10.2 | 17.7 | 226 | 214.7 | 214.7 | YES
28 | OK | 50 | 9 | 9 | 43 | 240.9 | 0.65 | 50 | 17 | 14.4 | 17.1 | 14.9 | 218.9 | 223.3 | 218.9 | YES
29 | OK | 26 | 25 | 25 | 43 | 88.2 | 1.54 | 50 | 17 | 14.4 | 17.1 | 15.6 | 220.8 | 222.1 | 220.8 | YES
30 | OK | 68 | 8 | 8 | 43 | 199.7 | 0.93 | 50 | 17 | 14.4 | 17.1 | 15.1 | 218.9 | 223.3 | 218.9 | YES
31 | OK | 6 | 1 | 66 | 43 | 234.2 | 9.3 | 50 | 17 | 14.4 | 10.9 | 17.7 | 225.5 | 214.7 | 214.7 | YES
32 | OK | 25 | 19 | 19 | 43 | 130.9 | 1.54 | 50 | 17 | 14.4 | 17 | 15.6 | 220.8 | 222.3 | 220.8 | YES
33 | OK | 1 | 0 | 66 | 43 | 234.2 | 6.92 | 50 | 17 | 14.4 | 13.2 | 17.3 | 224.1 | 216 | 216 | YES
34 | OK | 0 | 66 | 66 | 43 | 234.2 | 2.07 | 50 | 17 | 14.4 | 17 | 16 | 220.8 | 220.8 | 220.8 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 66-018267
TR_B (available) | 37-013799
TR_A Rated kVA | 100
TR_B Rated kVA | 160
TR_A Baseline Loading% | 17
TR_B Baseline Loading% | 14.4
Total Scenarios Evaluated | 41
Feasible Scenarios | 34
--- Optimal Solution ---
Switch Parent Node | 28
Switch Child Node | 88
Tie Node (TR_A side) | 89
Tie Node (TR_B side) | 43
Tie Line Distance (m) | 146.3
Load Transferred (kW) | 1.37
TR_A Loading After (%) | 15.4
TR_B Loading After (%) | 15.4
Minimum Voltage (V) | 221.1