## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 64 | 52 | 43 | 64 | 6.4 | 49.2 | 50 | 17 | 28.5 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 52 | 53 | 43 | 64 | 6.4 | 47.17 | 50 | 17 | 28.5 | [5 empty] | NO | TR_B sim: not converged
| NG | 53 | 65 | 43 | 64 | 6.4 | 42.51 | 50 | 17 | 28.5 | [5 empty] | NO | TR_B sim: not converged
| NG | 65 | 62 | 43 | 64 | 6.4 | 42.42 | 50 | 17 | 28.5 | [5 empty] | NO | TR_B sim: not converged
| NG | 62 | 40 | 43 | 64 | 6.4 | 41.43 | 50 | 17 | 28.5 | [5 empty] | NO | TR_B sim: not converged
| NG | 40 | 63 | 43 | 64 | 6.4 | 29.61 | 50 | 17 | 28.5 | [5 empty] | NO | TR_B sim: not converged
| NG | 63 | 60 | 43 | 64 | 6.4 | 29.61 | 50 | 17 | 28.5 | [5 empty] | NO | TR_B sim: not converged
1 | OK | 60 | 58 | 99 | 64 | 32.7 | 9.64 | 50 | 17 | 28.5 | 14.8 | 30.8 | 222.1 | 210 | 210 | YES
| NG | 60 | 61 | 43 | 64 | 6.4 | 19.85 | 50 | 17 | 28.5 | [5 empty] | NO | TR_B sim: not converged
2 | OK | 58 | 59 | 99 | 64 | 32.7 | 7.1 | 50 | 17 | 28.5 | 16.6 | 30.7 | 221 | 210 | 210 | YES
| NG | 61 | 5 | 43 | 64 | 6.4 | 19.85 | 50 | 17 | 28.5 | [5 empty] | NO | TR_B sim: not converged
3 | OK | 59 | 93 | 99 | 64 | 32.7 | 4.34 | 50 | 17 | 28.5 | 17 | 29 | 220.8 | 210.4 | 210.4 | YES
| NG | 5 | 4 | 43 | 64 | 6.4 | 18.75 | 50 | 17 | 28.5 | [5 empty] | NO | TR_B sim: not converged
4 | OK | 93 | 79 | 99 | 64 | 32.7 | 4.34 | 50 | 17 | 28.5 | 17 | 29 | 220.8 | 210.4 | 210.4 | YES
| NG | 4 | 91 | 43 | 64 | 6.4 | 16.4 | 50 | 17 | 28.5 | 17 | 49 | 220.8 | 138 | 138 | NO
5 | OK | 79 | 80 | 99 | 64 | 32.7 | 0.24 | 50 | 17 | 28.5 | 17 | 28.6 | 220.8 | 210.4 | 210.4 | YES
| NG | 79 | 78 | 78 | 64 | 68.6 | 4.1 | 50 | 17 | 28.5 | 17 | 31.7 | 220.8 | 202.4 | 202.4 | NO
| NG | 91 | 90 | 43 | 64 | 6.4 | 3.4 | 50 | 17 | 28.5 | 17 | 31.4 | 220.8 | 203.7 | 203.7 | NO
| NG | 91 | 44 | 36 | 59 | 26.1 | 13 | 50 | 17 | 28.5 | 17 | 41.1 | 220.8 | 179.6 | 179.6 | NO
6 | OK | 80 | 85 | 99 | 64 | 32.7 | 0.02 | 50 | 17 | 28.5 | 17 | 28.5 | 220.8 | 210.5 | 210.5 | YES
| NG | 78 | 77 | 77 | 64 | 77.4 | 3.31 | 50 | 17 | 28.5 | 17 | 31.4 | 220.8 | 203.3 | 203.3 | NO
| NG | 90 | 95 | 43 | 64 | 6.4 | 2.21 | 50 | 17 | 28.5 | 17 | 30.4 | 220.8 | 206.8 | 206.8 | NO
| NG | 44 | 33 | 36 | 59 | 26.1 | 12.62 | 50 | 17 | 28.5 | 17 | 40.7 | 220.8 | 180.9 | 180.9 | NO
7 | OK | 85 | 82 | 99 | 64 | 32.7 | 0.02 | 50 | 17 | 28.5 | 17 | 28.5 | 220.8 | 210.5 | 210.5 | YES
| NG | 77 | 72 | 72 | 64 | 115.2 | 3.14 | 50 | 17 | 28.5 | 17 | 31.2 | 220.8 | 203.7 | 203.7 | NO
| NG | 95 | 81 | 43 | 64 | 6.4 | 2.2 | 50 | 17 | 28.5 | 17 | 30.4 | 220.8 | 206.9 | 206.9 | NO
| NG | 33 | 34 | 36 | 59 | 26.1 | 12.28 | 50 | 17 | 28.5 | 17 | 40.3 | 220.8 | 182 | 182 | NO
8 | OK | 82 | 83 | 83 | 63 | 71.7 | 0.01 | 50 | 17 | 28.5 | 17 | 28.5 | 220.8 | 210.5 | 210.5 | YES
9 | OK | 82 | 98 | 99 | 64 | 32.7 | 0.01 | 50 | 17 | 28.5 | 17 | 28.5 | 220.8 | 210.5 | 210.5 | YES
| NG | 81 | 42 | 43 | 64 | 6.4 | 1.43 | 50 | 17 | 28.5 | 17 | 29.7 | 220.8 | 208.8 | 208.8 | NO
| NG | 34 | 35 | 36 | 59 | 26.1 | 5.29 | 50 | 17 | 28.5 | 17 | 33.1 | 220.8 | 202.4 | 202.4 | NO
10 | ** OPTIMAL ** | 98 | 99 | 99 | 64 | 32.7 | 0.01 | 50 | 17 | 28.5 | 17 | 28.5 | 220.8 | 210.5 | 210.5 | YES
11 | OK | 42 | 41 | 43 | 64 | 6.4 | 1.25 | 50 | 17 | 28.5 | 17 | 29 | 220.8 | 210.5 | 210.5 | YES
| NG | 35 | 10 | 36 | 59 | 26.1 | 4.92 | 50 | 17 | 28.5 | 17 | 32.7 | 220.8 | 203.2 | 203.2 | NO
12 | OK | 41 | 3 | 3 | 64 | 47.1 | 0.6 | 50 | 17 | 28.5 | 17 | 29 | 220.8 | 210.5 | 210.5 | YES
| NG | 10 | 11 | 11 | 59 | 67.5 | 3 | 50 | 17 | 28.5 | 17 | 31 | 220.8 | 207.6 | 207.6 | NO
| NG | 10 | 12 | 36 | 59 | 26.1 | 1.92 | 50 | 17 | 28.5 | 17 | 30.1 | 220.8 | 209.2 | 209.2 | NO
13 | OK | 11 | 37 | 37 | 59 | 84 | 0.51 | 50 | 17 | 28.5 | 17 | 28.9 | 220.8 | 210.5 | 210.5 | YES
14 | OK | 12 | 36 | 36 | 59 | 26.1 | 0.29 | 50 | 17 | 28.5 | 17 | 28.7 | 220.8 | 210.5 | 210.5 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 66-018267
TR_B (available) | 51-007132
TR_A Rated kVA | 100
TR_B Rated kVA | 160
TR_A Baseline Loading% | 17
TR_B Baseline Loading% | 28.5
Total Scenarios Evaluated | 39
Feasible Scenarios | 14
--- Optimal Solution ---
Switch Parent Node | 98
Switch Child Node | 99
Tie Node (TR_A side) | 99
Tie Node (TR_B side) | 64
Tie Line Distance (m) | 32.7
Load Transferred (kW) | 0.01
TR_A Loading After (%) | 17
TR_B Loading After (%) | 28.5
Minimum Voltage (V) | 210.5