## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 84 | 59 | 62 | 48 | 39.9 | 20.97 | 50 | 83.1 | 25.3 | 34.6 | 52.4 | 218.7 | 192.7 | 192.7 | NO
| NG | 59 | 16 | 62 | 48 | 39.9 | 19.59 | 50 | 83.1 | 25.3 | 37.7 | 50.6 | 218.2 | 191.4 | 191.4 | NO
| NG | 16 | 17 | 62 | 48 | 39.9 | 12.07 | 50 | 83.1 | 25.3 | 55 | 40.3 | 216.9 | 203.4 | 203.4 | NO
1 | OK | 16 | 8 | 97 | 48 | 63.7 | 5.46 | 50 | 83.1 | 25.3 | 70.5 | 31.9 | 216.2 | 214.7 | 214.7 | YES
2 | ** OPTIMAL ** | 16 | 103 | 23 | 50 | 55.8 | 2.06 | 50 | 83.1 | 25.3 | 78.4 | 27.8 | 216.1 | 222.4 | 216.1 | YES
| NG | 17 | 14 | 62 | 48 | 39.9 | 10.92 | 50 | 83.1 | 25.3 | 57.7 | 38.7 | 216.9 | 207.5 | 207.5 | NO
3 | OK | 8 | 9 | 97 | 48 | 63.7 | 1.98 | 50 | 83.1 | 25.3 | 78.5 | 27.7 | 215.6 | 220.3 | 215.6 | YES
4 | OK | 103 | 104 | 23 | 50 | 55.8 | 1.83 | 50 | 83.1 | 25.3 | 78.9 | 27.5 | 216 | 222.2 | 216 | YES
| NG | 14 | 15 | 62 | 48 | 39.9 | 10.92 | 50 | 83.1 | 25.3 | 57.7 | 38.7 | 216.9 | 207.5 | 207.5 | NO
5 | OK | 9 | 43 | 97 | 48 | 63.7 | 1.98 | 50 | 83.1 | 25.3 | 78.5 | 27.7 | 215.6 | 220.3 | 215.6 | YES
6 | OK | 104 | 26 | 23 | 50 | 55.8 | 1.72 | 50 | 83.1 | 25.3 | 79.1 | 27.4 | 216 | 222.2 | 216 | YES
| NG | 15 | 60 | 62 | 48 | 39.9 | 10.5 | 50 | 83.1 | 25.3 | 58.6 | 38.2 | 216.8 | 207.4 | 207.4 | NO
7 | OK | 26 | 56 | 23 | 50 | 55.8 | 1.72 | 50 | 83.1 | 25.3 | 79.1 | 27.4 | 216 | 222.2 | 216 | YES
| NG | 60 | 61 | 62 | 48 | 39.9 | 10.19 | 50 | 83.1 | 25.3 | 59.3 | 37.8 | 216.8 | 208.2 | 208.2 | NO
| NG | 61 | 62 | 62 | 48 | 39.9 | 7.44 | 50 | 83.1 | 25.3 | 65.7 | 34.5 | 215.9 | 207.8 | 207.8 | NO
| NG | 62 | 63 | 63 | 48 | 42.4 | 6.71 | 50 | 83.1 | 25.3 | 67.3 | 33.6 | 215.9 | 208.1 | 208.1 | NO
8 | OK | 63 | 66 | 66 | 48 | 65.7 | 4.7 | 50 | 83.1 | 25.3 | 72 | 31 | 215.9 | 214.9 | 214.9 | YES
9 | OK | 66 | 67 | 69 | 9 | 88 | 3.45 | 50 | 83.1 | 25.3 | 74.9 | 27.8 | 215.6 | 215.1 | 215.1 | YES
10 | OK | 67 | 68 | 69 | 9 | 88 | 3.36 | 50 | 83.1 | 25.3 | 75.1 | 27.8 | 215.6 | 215.1 | 215.1 | YES
11 | OK | 68 | 69 | 69 | 9 | 88 | 2.89 | 50 | 83.1 | 25.3 | 76.2 | 27.4 | 215.6 | 216.2 | 215.6 | YES
12 | OK | 69 | 13 | 13 | 10 | 107.1 | 2.82 | 50 | 83.1 | 25.3 | 76.4 | 27.3 | 215.6 | 216.8 | 215.6 | YES
13 | OK | 13 | 11 | 82 | 10 | 145.3 | 1.83 | 50 | 83.1 | 25.3 | 78.7 | 27.3 | 215.6 | 216.6 | 215.6 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 66-022069
TR_B (available) | 35-007298
TR_A Rated kVA | 50
TR_B Rated kVA | 100
TR_A Baseline Loading% | 83.1
TR_B Baseline Loading% | 25.3
Total Scenarios Evaluated | 22
Feasible Scenarios | 13
--- Optimal Solution ---
Switch Parent Node | 16
Switch Child Node | 103
Tie Node (TR_A side) | 23
Tie Node (TR_B side) | 50
Tie Line Distance (m) | 55.8
Load Transferred (kW) | 2.06
TR_A Loading After (%) | 78.4
TR_B Loading After (%) | 27.8
Minimum Voltage (V) | 216.1