## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 16 | 17 | 73 | 14 | 20.1 | 12.07 | 50 | 83.1 | 37.5 | 55 | 49 | 216.9 | 209.7 | 209.7 | NO
| NG | 17 | 14 | 73 | 14 | 20.1 | 10.92 | 50 | 83.1 | 37.5 | 57.7 | 49 | 216.9 | 209.7 | 209.7 | NO
| NG | 14 | 15 | 73 | 14 | 20.1 | 10.92 | 50 | 83.1 | 37.5 | 57.7 | 49 | 216.9 | 209.7 | 209.7 | NO
1 | OK | 15 | 60 | 73 | 14 | 20.1 | 10.5 | 50 | 83.1 | 37.5 | 58.6 | 48.5 | 216.8 | 210.3 | 210.3 | YES
2 | OK | 60 | 61 | 73 | 14 | 20.1 | 10.19 | 50 | 83.1 | 37.5 | 59.3 | 48.3 | 216.8 | 210.6 | 210.6 | YES
3 | ** OPTIMAL ** | 61 | 62 | 73 | 14 | 20.1 | 7.44 | 50 | 83.1 | 37.5 | 65.7 | 41.1 | 215.9 | 219.8 | 215.9 | YES
4 | OK | 62 | 63 | 73 | 14 | 20.1 | 6.71 | 50 | 83.1 | 37.5 | 67.3 | 40.9 | 215.9 | 219.9 | 215.9 | YES
5 | OK | 63 | 66 | 73 | 14 | 20.1 | 4.7 | 50 | 83.1 | 37.5 | 72 | 40.9 | 215.9 | 219.9 | 215.9 | YES
6 | OK | 66 | 67 | 73 | 14 | 20.1 | 3.45 | 50 | 83.1 | 37.5 | 74.9 | 38.6 | 215.6 | 222.6 | 215.6 | YES
7 | OK | 67 | 68 | 73 | 14 | 20.1 | 3.36 | 50 | 83.1 | 37.5 | 75.1 | 38.2 | 215.6 | 223 | 215.6 | YES
8 | OK | 68 | 69 | 73 | 14 | 20.1 | 2.89 | 50 | 83.1 | 37.5 | 76.2 | 38.2 | 215.6 | 223 | 215.6 | YES
9 | OK | 69 | 13 | 73 | 14 | 20.1 | 2.82 | 50 | 83.1 | 37.5 | 76.4 | 38.2 | 215.6 | 223 | 215.6 | YES
10 | OK | 13 | 11 | 73 | 14 | 20.1 | 1.83 | 50 | 83.1 | 37.5 | 78.7 | 38.2 | 215.6 | 223 | 215.6 | YES
11 | OK | 11 | 12 | 12 | 41 | 141.8 | 1.66 | 50 | 83.1 | 37.5 | 79.1 | 37.6 | 215.5 | 223.4 | 215.5 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 66-022069
TR_B (available) | 43-002708
TR_A Rated kVA | 50
TR_B Rated kVA | 30
TR_A Baseline Loading% | 83.1
TR_B Baseline Loading% | 37.5
Total Scenarios Evaluated | 14
Feasible Scenarios | 11
--- Optimal Solution ---
Switch Parent Node | 61
Switch Child Node | 62
Tie Node (TR_A side) | 73
Tie Node (TR_B side) | 14
Tie Line Distance (m) | 20.1
Load Transferred (kW) | 7.44
TR_A Loading After (%) | 65.7
TR_B Loading After (%) | 41.1
Minimum Voltage (V) | 215.9