## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 54 | 33 | 47 | 18 | 2.1 | 16.59 | 50 | 93.2 | 19.8 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 33 | 34 | 47 | 18 | 2.1 | 16.59 | 50 | 93.2 | 19.8 | 54.7 | 48 | 217.7 | 214 | 214 | YES
| NG | 34 | 52 | 47 | 18 | 2.1 | 15.35 | 50 | 93.2 | 19.8 | 0 | 47.2 | 6 | 214.2 | 6 | NO
2 | OK | 52 | 35 | 47 | 18 | 2.1 | 15.35 | 50 | 93.2 | 19.8 | 57.6 | 47.2 | 217.7 | 214.2 | 214.2 | YES
3 | OK | 35 | 36 | 47 | 18 | 2.1 | 14.31 | 50 | 93.2 | 19.8 | 59.9 | 46.8 | 217.2 | 214.3 | 214.3 | YES
4 | OK | 36 | 37 | 47 | 18 | 2.1 | 11.65 | 50 | 93.2 | 19.8 | 66 | 39.6 | 217.2 | 215.8 | 215.8 | YES
5 | OK | 37 | 38 | 47 | 18 | 2.1 | 10.97 | 50 | 93.2 | 19.8 | 67.6 | 38.6 | 217 | 216 | 216 | YES
6 | ** OPTIMAL ** | 38 | 39 | 47 | 18 | 2.1 | 9.54 | 50 | 93.2 | 19.8 | 68.7 | 33.9 | 217 | 217 | 217 | YES
7 | OK | 39 | 40 | 47 | 18 | 2.1 | 8.42 | 50 | 93.2 | 19.8 | 73.5 | 33.4 | 216.9 | 217.1 | 216.9 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 67-004277
TR_B (available) | 55-005332
TR_A Rated kVA | 50
TR_B Rated kVA | 30
TR_A Baseline Loading% | 93.2
TR_B Baseline Loading% | 19.8
Total Scenarios Evaluated | 9
Feasible Scenarios | 7
--- Optimal Solution ---
Switch Parent Node | 38
Switch Child Node | 39
Tie Node (TR_A side) | 47
Tie Node (TR_B side) | 18
Tie Line Distance (m) | 2.1
Load Transferred (kW) | 9.54
TR_A Loading After (%) | 68.7
TR_B Loading After (%) | 33.9
Minimum Voltage (V) | 217