## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 12 | 13 | 7 | 13 | 3.8 | 19.3 | 50 | 79.5 | 20.1 | 34.9 | 34.5 | 219 | 213.6 | 213.6 | YES
2 | OK | 13 | 10 | 7 | 13 | 3.8 | 9.36 | 50 | 79.5 | 20.1 | 57.8 | 26.8 | 218.8 | 221.8 | 218.8 | YES
3 | ** OPTIMAL ** | 10 | 11 | 7 | 13 | 3.8 | 9.36 | 50 | 79.5 | 20.1 | 57.8 | 26.8 | 218.8 | 221.8 | 218.8 | YES
4 | OK | 11 | 19 | 7 | 13 | 3.8 | 8.47 | 50 | 79.5 | 20.1 | 59.8 | 26.2 | 218.5 | 221.8 | 218.5 | YES
5 | OK | 19 | 22 | 7 | 13 | 3.8 | 8.47 | 50 | 79.5 | 20.1 | 59.8 | 26.2 | 218.5 | 221.8 | 218.5 | YES
6 | OK | 22 | 20 | 7 | 13 | 3.8 | 8.47 | 50 | 79.5 | 20.1 | 59.8 | 26.2 | 218.5 | 221.8 | 218.5 | YES
7 | OK | 20 | 8 | 7 | 13 | 3.8 | 8.47 | 50 | 79.5 | 20.1 | 59.8 | 26.2 | 218.5 | 221.8 | 218.5 | YES
8 | OK | 8 | 9 | 7 | 13 | 3.8 | 6.09 | 50 | 79.5 | 20.1 | 65.3 | 24.5 | 218.2 | 221.7 | 218.2 | YES
9 | OK | 9 | 17 | 7 | 13 | 3.8 | 5.4 | 50 | 79.5 | 20.1 | 66.9 | 24 | 218.2 | 221.7 | 218.2 | YES
10 | OK | 17 | 18 | 7 | 13 | 3.8 | 5 | 50 | 79.5 | 20.1 | 67.9 | 23.7 | 218 | 221.7 | 218 | YES
11 | OK | 18 | 0 | 7 | 13 | 3.8 | 5 | 50 | 79.5 | 20.1 | 67.9 | 23.7 | 218 | 221.7 | 218 | YES
12 | OK | 0 | 1 | 7 | 13 | 3.8 | 5 | 50 | 79.5 | 20.1 | 67.9 | 23.7 | 218 | 221.7 | 218 | YES
13 | OK | 1 | 6 | 7 | 13 | 3.8 | 2.96 | 50 | 79.5 | 20.1 | 72.5 | 22.2 | 218 | 222.1 | 218 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 67-013158
TR_B (available) | 42-004976
TR_A Rated kVA | 50
TR_B Rated kVA | 160
TR_A Baseline Loading% | 79.5
TR_B Baseline Loading% | 20.1
Total Scenarios Evaluated | 13
Feasible Scenarios | 13
--- Optimal Solution ---
Switch Parent Node | 10
Switch Child Node | 11
Tie Node (TR_A side) | 7
Tie Node (TR_B side) | 13
Tie Line Distance (m) | 3.8
Load Transferred (kW) | 9.36
TR_A Loading After (%) | 57.8
TR_B Loading After (%) | 26.8
Minimum Voltage (V) | 218.8