## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 15 | 14 | 9 | 3 | 61.5 | 19.98 | 50 | 56.6 | 14.4 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 15 | 13 | 12 | 3 | 5.1 | 4.01 | 50 | 56.6 | 14.4 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 14 | 20 | 9 | 3 | 61.5 | 19.98 | 50 | 56.6 | 14.4 | 9.2 | 29.5 | 227.5 | 210.8 | 210.8 | YES
2 | OK | 13 | 10 | 12 | 3 | 5.1 | 3.78 | 50 | 56.6 | 14.4 | 47.9 | 17.1 | 215.4 | 216 | 215.4 | YES
3 | OK | 20 | 16 | 9 | 3 | 61.5 | 19.98 | 50 | 56.6 | 14.4 | 9.2 | 29.5 | 227.5 | 210.8 | 210.8 | YES
4 | OK | 10 | 11 | 12 | 3 | 5.1 | 2.99 | 50 | 56.6 | 14.4 | 49.7 | 16.5 | 215 | 215.9 | 215 | YES
5 | ** OPTIMAL ** | 16 | 17 | 9 | 3 | 61.5 | 6.69 | 50 | 56.6 | 14.4 | 40.4 | 19.2 | 218.6 | 216.4 | 216.4 | YES
6 | OK | 11 | 12 | 12 | 3 | 5.1 | 0.43 | 50 | 56.6 | 14.4 | 55.6 | 14.7 | 213.6 | 215.8 | 213.6 | YES
7 | OK | 17 | 7 | 9 | 3 | 61.5 | 6.69 | 50 | 56.6 | 14.4 | 40.4 | 19.2 | 218.6 | 216.4 | 216.4 | YES
8 | OK | 7 | 8 | 9 | 3 | 61.5 | 2.71 | 50 | 56.6 | 14.4 | 50.1 | 16.3 | 213.2 | 216.2 | 213.2 | YES
9 | OK | 8 | 9 | 9 | 3 | 61.5 | 1.65 | 50 | 56.6 | 14.4 | 52.6 | 15.5 | 213.3 | 216 | 213.3 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 67-013169
TR_B (available) | 66-025967
TR_A Rated kVA | 50
TR_B Rated kVA | 160
TR_A Baseline Loading% | 56.6
TR_B Baseline Loading% | 14.4
Total Scenarios Evaluated | 11
Feasible Scenarios | 9
--- Optimal Solution ---
Switch Parent Node | 16
Switch Child Node | 17
Tie Node (TR_A side) | 9
Tie Node (TR_B side) | 3
Tie Line Distance (m) | 61.5
Load Transferred (kW) | 6.69
TR_A Loading After (%) | 40.4
TR_B Loading After (%) | 19.2
Minimum Voltage (V) | 216.4