## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 16 | 0 | 47 | 69 | 2 | 29.14 | 50 | 87.2 | 28.5 | 18.1 | 42.4 | 221.1 | 187.9 | 187.9 | NO
| NG | 16 | 15 | 15 | 73 | 119.1 | 7.8 | 50 | 87.2 | 28.5 | 69 | 31.6 | 204 | 214.8 | 204 | NO
| NG | 0 | 1 | 37 | 8 | 40 | 6.63 | 50 | 87.2 | 28.5 | 71.6 | 33.6 | 205.3 | 215.6 | 205.3 | NO
| NG | 0 | 9 | 9 | 73 | 93.8 | 3.69 | 50 | 87.2 | 28.5 | 78.7 | 29.3 | 202.5 | 219.7 | 202.5 | NO
| NG | 0 | 13 | 47 | 69 | 2 | 18.82 | 50 | 87.2 | 28.5 | 41.9 | 36.9 | 218.3 | 205.5 | 205.5 | NO
| NG | 15 | 14 | 14 | 73 | 149.9 | 4.68 | 50 | 87.2 | 28.5 | 76.2 | 31.6 | 204 | 214.8 | 204 | NO
| NG | 1 | 24 | 37 | 8 | 40 | 6.44 | 50 | 87.2 | 28.5 | 72 | 33.5 | 205.3 | 215.5 | 205.3 | NO
| NG | 13 | 12 | 47 | 69 | 2 | 18.42 | 50 | 87.2 | 28.5 | 42.8 | 36.9 | 218.3 | 205.5 | 205.5 | NO
| NG | 24 | 17 | 37 | 8 | 40 | 5.67 | 50 | 87.2 | 28.5 | 73.8 | 32.9 | 204.7 | 217.2 | 204.7 | NO
| NG | 12 | 8 | 47 | 69 | 2 | 18.42 | 50 | 87.2 | 28.5 | 42.8 | 36.9 | 218.3 | 205.5 | 205.5 | NO
| NG | 17 | 18 | 37 | 8 | 40 | 4.83 | 50 | 87.2 | 28.5 | 75.8 | 32.2 | 204.1 | 218.6 | 204.1 | NO
| NG | 8 | 3 | 47 | 69 | 2 | 17.59 | 50 | 87.2 | 28.5 | 44.7 | 36.4 | 218 | 206.5 | 206.5 | NO
| NG | 3 | 2 | 47 | 69 | 2 | 16.87 | 50 | 87.2 | 28.5 | 46.4 | 36.4 | 218 | 206.5 | 206.5 | NO
| NG | 2 | 25 | 47 | 69 | 2 | 16.56 | 50 | 87.2 | 28.5 | 47.1 | 36.4 | 218 | 206.5 | 206.5 | NO
| NG | 25 | 48 | 47 | 69 | 2 | 16.56 | 50 | 87.2 | 28.5 | 47.1 | 36.4 | 218 | 206.5 | 206.5 | NO
| NG | 48 | 47 | 47 | 69 | 2 | 16.56 | 50 | 87.2 | 28.5 | 47.1 | 36.4 | 218 | 206.5 | 206.5 | NO
1 | ** OPTIMAL ** | 47 | 46 | 41 | 67 | 2.2 | 13.64 | 50 | 87.2 | 28.5 | 53.9 | 34.3 | 216.8 | 216.8 | 216.8 | YES
2 | OK | 46 | 45 | 41 | 67 | 2.2 | 9.86 | 50 | 87.2 | 28.5 | 62.8 | 32.8 | 215.8 | 219.9 | 215.8 | YES
3 | OK | 45 | 39 | 41 | 67 | 2.2 | 8.75 | 50 | 87.2 | 28.5 | 65.4 | 32.8 | 215.8 | 219.9 | 215.8 | YES
4 | OK | 39 | 38 | 41 | 67 | 2.2 | 6.58 | 50 | 87.2 | 28.5 | 70.5 | 32.7 | 215.8 | 219.9 | 215.8 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 67-013172
TR_B (available) | 59-011599
TR_A Rated kVA | 50
TR_B Rated kVA | 160
TR_A Baseline Loading% | 87.2
TR_B Baseline Loading% | 28.5
Total Scenarios Evaluated | 20
Feasible Scenarios | 4
--- Optimal Solution ---
Switch Parent Node | 47
Switch Child Node | 46
Tie Node (TR_A side) | 41
Tie Node (TR_B side) | 67
Tie Line Distance (m) | 2.2
Load Transferred (kW) | 13.64
TR_A Loading After (%) | 53.9
TR_B Loading After (%) | 34.3
Minimum Voltage (V) | 216.8