## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 16 | 29 | 25 | 10 | 17.7 | 10.1 | 50 | 83 | 32.3 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 29 | 30 | 25 | 10 | 17.7 | 9.24 | 50 | 83 | 32.3 | 61.8 | 39.3 | 220 | 216.5 | 216.5 | YES
2 | OK | 30 | 31 | 25 | 10 | 17.7 | 9.24 | 50 | 83 | 32.3 | 61.8 | 39.3 | 220 | 216.5 | 216.5 | YES
3 | OK | 31 | 17 | 25 | 10 | 17.7 | 7.93 | 50 | 83 | 32.3 | 64.3 | 38.3 | 219.5 | 219.1 | 219.1 | YES
4 | ** OPTIMAL ** | 17 | 18 | 25 | 10 | 17.7 | 7.42 | 50 | 83 | 32.3 | 65.9 | 37.9 | 219.1 | 220.1 | 219.1 | YES
5 | OK | 18 | 20 | 25 | 10 | 17.7 | 6.9 | 50 | 83 | 32.3 | 67.1 | 37.5 | 218.9 | 221 | 218.9 | YES
6 | OK | 20 | 21 | 22 | 5 | 22 | 2.11 | 50 | 83 | 32.3 | 78.1 | 33.5 | 218.6 | 220.9 | 218.6 | YES
7 | OK | 20 | 23 | 25 | 10 | 17.7 | 4.79 | 50 | 83 | 32.3 | 70.6 | 35.9 | 218.1 | 222.4 | 218.1 | YES
8 | OK | 23 | 2 | 25 | 10 | 17.7 | 4.79 | 50 | 83 | 32.3 | 72 | 35.9 | 218.1 | 222.4 | 218.1 | YES
9 | OK | 2 | 35 | 25 | 10 | 17.7 | 1.84 | 50 | 83 | 32.3 | 78.8 | 33 | 218.1 | 222.6 | 218.1 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 67-014484
TR_B (available) | 38-023388
TR_A Rated kVA | 50
TR_B Rated kVA | 160
TR_A Baseline Loading% | 83
TR_B Baseline Loading% | 32.3
Total Scenarios Evaluated | 10
Feasible Scenarios | 9
--- Optimal Solution ---
Switch Parent Node | 17
Switch Child Node | 18
Tie Node (TR_A side) | 25
Tie Node (TR_B side) | 10
Tie Line Distance (m) | 17.7
Load Transferred (kW) | 7.42
TR_A Loading After (%) | 65.9
TR_B Loading After (%) | 37.9
Minimum Voltage (V) | 219.1