## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 16 | 29 | 20 | 50 | 6.5 | 10.1 | 95 | 83 | 20.1 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 29 | 30 | 20 | 50 | 6.5 | 9.24 | 95 | 83 | 20.1 | 61.8 | 26.8 | 220 | 226.5 | 220 | YES
2 | ** OPTIMAL ** | 30 | 31 | 20 | 50 | 6.5 | 9.24 | 95 | 83 | 20.1 | 61.8 | 26.8 | 220 | 226.5 | 220 | YES
3 | OK | 31 | 17 | 20 | 50 | 6.5 | 7.93 | 95 | 83 | 20.1 | 64.3 | 25.8 | 219.5 | 226.9 | 219.5 | YES
4 | OK | 17 | 18 | 20 | 50 | 6.5 | 7.42 | 95 | 83 | 20.1 | 65.9 | 25.4 | 219.1 | 226.8 | 219.1 | YES
5 | OK | 18 | 20 | 20 | 50 | 6.5 | 6.9 | 95 | 83 | 20.1 | 67.1 | 25.1 | 218.9 | 226.8 | 218.9 | YES
6 | OK | 20 | 21 | 21 | 50 | 10.8 | 2.11 | 50 | 83 | 20.1 | 78.1 | 21.2 | 218.6 | 227.4 | 218.6 | YES
7 | OK | 20 | 23 | 23 | 50 | 24 | 4.79 | 95 | 83 | 20.1 | 70.6 | 23.5 | 218.1 | 226.8 | 218.1 | YES
8 | OK | 23 | 2 | 2 | 50 | 39.9 | 4.79 | 95 | 83 | 20.1 | 72 | 23.5 | 218.1 | 226.8 | 218.1 | YES
9 | OK | 2 | 35 | 35 | 50 | 46 | 1.84 | 50 | 83 | 20.1 | 78.8 | 20.7 | 218.1 | 227.3 | 218.1 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 67-014484
TR_B (available) | 45-022642
TR_A Rated kVA | 50
TR_B Rated kVA | 160
TR_A Baseline Loading% | 83
TR_B Baseline Loading% | 20.1
Total Scenarios Evaluated | 10
Feasible Scenarios | 9
--- Optimal Solution ---
Switch Parent Node | 30
Switch Child Node | 31
Tie Node (TR_A side) | 20
Tie Node (TR_B side) | 50
Tie Line Distance (m) | 6.5
Load Transferred (kW) | 9.24
TR_A Loading After (%) | 61.8
TR_B Loading After (%) | 26.8
Minimum Voltage (V) | 220