## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 16 | 15 | 6 | 86 | 26.1 | 24.95 | 50 | 83 | 56.5 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 16 | 29 | 14 | 76 | 2.8 | 10.1 | 50 | 83 | 56.5 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 15 | 34 | 6 | 86 | 26.1 | 24.95 | 50 | 83 | 56.5 | 24.9 | 64 | 227.5 | 200.9 | 200.9 | NO
1 | OK | 29 | 30 | 14 | 76 | 2.8 | 9.24 | 50 | 83 | 56.5 | 61.8 | 60 | 220 | 211 | 211 | YES
| NG | 34 | 13 | 6 | 86 | 26.1 | 24.79 | 50 | 83 | 56.5 | 25.3 | 64 | 227.5 | 201 | 201 | NO
2 | OK | 30 | 31 | 14 | 76 | 2.8 | 9.24 | 50 | 83 | 56.5 | 61.8 | 60 | 220 | 211 | 211 | YES
| NG | 13 | 12 | 6 | 86 | 26.1 | 24.76 | 50 | 83 | 56.5 | 25.3 | 64 | 227.5 | 201 | 201 | NO
3 | OK | 31 | 17 | 14 | 76 | 2.8 | 7.93 | 50 | 83 | 56.5 | 64.3 | 59 | 219.5 | 212 | 212 | YES
| NG | 12 | 9 | 6 | 86 | 26.1 | 21.87 | 50 | 83 | 56.5 | 32 | 64 | 226.5 | 201 | 201 | NO
4 | OK | 17 | 18 | 14 | 76 | 2.8 | 7.42 | 50 | 83 | 56.5 | 65.9 | 58.6 | 219.1 | 212.3 | 212.3 | YES
| NG | 9 | 8 | 6 | 86 | 26.1 | 20.75 | 50 | 83 | 56.5 | 34.5 | 64 | 225.7 | 201 | 201 | NO
5 | ** OPTIMAL ** | 18 | 20 | 14 | 76 | 2.8 | 6.9 | 50 | 83 | 56.5 | 67.1 | 58.2 | 218.9 | 212.4 | 212.4 | YES
| NG | 8 | 28 | 6 | 86 | 26.1 | 19.58 | 50 | 83 | 56.5 | 37.2 | 63.1 | 225.6 | 203.5 | 203.5 | NO
6 | OK | 20 | 21 | 22 | 76 | 62.8 | 2.11 | 50 | 83 | 56.5 | 78.1 | 57.7 | 218.6 | 212.3 | 212.3 | YES
7 | OK | 20 | 23 | 14 | 76 | 2.8 | 4.79 | 50 | 83 | 56.5 | 70.6 | 57 | 218.1 | 212.1 | 212.1 | YES
| NG | 28 | 10 | 6 | 86 | 26.1 | 19.07 | 50 | 83 | 56.5 | 38.4 | 62.6 | 225.6 | 204.7 | 204.7 | NO
8 | OK | 23 | 2 | 14 | 76 | 2.8 | 4.79 | 50 | 83 | 56.5 | 72 | 57 | 218.1 | 212.1 | 212.1 | YES
| NG | 10 | 11 | 6 | 86 | 26.1 | 13.72 | 50 | 83 | 56.5 | 50.8 | 59.8 | 223.8 | 209 | 209 | NO
9 | OK | 2 | 35 | 25 | 76 | 22.4 | 1.84 | 50 | 83 | 56.5 | 78.8 | 57 | 218.1 | 212.1 | 212.1 | YES
| NG | 11 | 32 | 6 | 86 | 26.1 | 13 | 50 | 83 | 56.5 | 52.5 | 59.5 | 223.6 | 209.5 | 209.5 | NO
| NG | 32 | 33 | 6 | 86 | 26.1 | 10.99 | 50 | 83 | 56.5 | 57.1 | 41.9 | 223.4 | 10 | 10 | NO
| NG | 33 | 19 | 6 | 86 | 26.1 | 7.44 | 50 | 83 | 56.5 | 65.4 | 59.4 | 222.7 | 209.7 | 209.7 | NO
10 | OK | 19 | 7 | 6 | 86 | 26.1 | 5.59 | 50 | 83 | 56.5 | 69.7 | 58.7 | 222.7 | 210.7 | 210.7 | YES
11 | OK | 7 | 6 | 6 | 86 | 26.1 | 2.48 | 50 | 83 | 56.5 | 77.1 | 57.6 | 219.9 | 212.1 | 212.1 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 67-014484
TR_B (available) | 65-006849
TR_A Rated kVA | 50
TR_B Rated kVA | 160
TR_A Baseline Loading% | 83
TR_B Baseline Loading% | 56.5
Total Scenarios Evaluated | 24
Feasible Scenarios | 11
--- Optimal Solution ---
Switch Parent Node | 18
Switch Child Node | 20
Tie Node (TR_A side) | 14
Tie Node (TR_B side) | 76
Tie Line Distance (m) | 2.8
Load Transferred (kW) | 6.9
TR_A Loading After (%) | 67.1
TR_B Loading After (%) | 58.2
Minimum Voltage (V) | 212.4