## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 25 | 24 | 0 | 86 | 2.4 | 36.58 | 50 | 58.3 | 31.2 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 24 | 47 | 0 | 86 | 2.4 | 36.58 | 50 | 58.3 | 31.2 | 15 | 59.3 | 228.5 | 210.1 | 210.1 | YES
2 | OK | 47 | 48 | 0 | 86 | 2.4 | 36.58 | 50 | 58.3 | 31.2 | 15 | 59.3 | 228.5 | 210.1 | 210.1 | YES
3 | OK | 48 | 14 | 0 | 86 | 2.4 | 36.58 | 50 | 58.3 | 31.2 | 15 | 59.3 | 228.5 | 210.1 | 210.1 | YES
4 | OK | 14 | 13 | 0 | 86 | 2.4 | 34.45 | 50 | 58.3 | 31.2 | 17.4 | 57.5 | 228.2 | 211.6 | 211.6 | YES
5 | OK | 13 | 12 | 0 | 86 | 2.4 | 33.93 | 50 | 58.3 | 31.2 | 18 | 57.1 | 228.2 | 211.6 | 211.6 | YES
6 | OK | 12 | 26 | 0 | 86 | 2.4 | 32.26 | 50 | 58.3 | 31.2 | 19.9 | 55.8 | 228.2 | 211.4 | 211.4 | YES
7 | OK | 26 | 11 | 0 | 86 | 2.4 | 27.5 | 50 | 58.3 | 31.2 | 25.4 | 51.8 | 227.5 | 214 | 214 | YES
8 | OK | 11 | 10 | 0 | 86 | 2.4 | 27.22 | 50 | 58.3 | 31.2 | 25.7 | 51.8 | 227.3 | 214 | 214 | YES
9 | OK | 10 | 6 | 0 | 86 | 2.4 | 26.38 | 50 | 58.3 | 31.2 | 26.7 | 51.1 | 227.5 | 214 | 214 | YES
10 | OK | 6 | 5 | 0 | 86 | 2.4 | 24.83 | 50 | 58.3 | 31.2 | 28.5 | 49.9 | 226.6 | 214.7 | 214.7 | YES
11 | OK | 5 | 2 | 0 | 86 | 2.4 | 23.03 | 50 | 58.3 | 31.2 | 28.5 | 48.5 | 226.6 | 215.7 | 215.7 | YES
12 | OK | 2 | 3 | 3 | 104 | 54.7 | 22.75 | 95 | 58.3 | 31.2 | 30.9 | 48 | 226.6 | 219.7 | 219.7 | YES
13 | OK | 3 | 4 | 4 | 104 | 57.1 | 2.39 | 95 | 58.3 | 31.2 | 54.5 | 32.9 | 217.4 | 221.8 | 217.4 | YES
14 | OK | 3 | 15 | 15 | 104 | 80.5 | 19.66 | 95 | 58.3 | 31.2 | 34.5 | 45.6 | 224.8 | 219.3 | 219.3 | YES
15 | OK | 4 | 31 | 31 | 104 | 58.1 | 2.39 | 95 | 58.3 | 31.2 | 55.4 | 32.2 | 217.4 | 221.8 | 217.4 | YES
16 | OK | 15 | 36 | 36 | 104 | 87.7 | 0.45 | 95 | 58.3 | 31.2 | 57.8 | 31.5 | 216.2 | 222.1 | 216.2 | YES
17 | ** OPTIMAL ** | 15 | 37 | 37 | 104 | 84.4 | 18.23 | 95 | 58.3 | 31.2 | 35 | 44.6 | 224.6 | 220.8 | 220.8 | YES
18 | OK | 31 | 9 | 9 | 104 | 61.6 | 1.38 | 95 | 58.3 | 31.2 | 56.6 | 32.2 | 216.1 | 221.8 | 216.1 | YES
| NG | 36 | 38 | 38 | 104 | 88.9 | 0.22 | 95 | 58.3 | 31.2 | 58.1 | 3.1 | 215.9 | 7.1 | 7.1 | NO
19 | OK | 37 | 35 | 35 | 104 | 86.7 | 18.23 | 50 | 58.3 | 31.2 | 35 | 44.6 | 224.6 | 220.3 | 220.3 | YES
20 | OK | 9 | 7 | 7 | 104 | 69.1 | 0.16 | 95 | 58.3 | 31.2 | 58.1 | 31.3 | 216.2 | 222.1 | 216.2 | YES
21 | OK | 35 | 17 | 17 | 104 | 104.1 | 17.2 | 95 | 58.3 | 31.2 | 37.4 | 43.8 | 224.1 | 220.5 | 220.5 | YES
22 | OK | 17 | 16 | 16 | 104 | 116.9 | 16.89 | 95 | 58.3 | 31.2 | 37.8 | 43.6 | 224.2 | 220.5 | 220.5 | YES
23 | OK | 16 | 34 | 34 | 86 | 124.6 | 16.33 | 50 | 58.3 | 31.2 | 37.8 | 43.4 | 224.2 | 217.3 | 217.3 | YES
24 | OK | 34 | 33 | 33 | 86 | 126.9 | 15.52 | 50 | 58.3 | 31.2 | 37.8 | 42.8 | 224.2 | 217.6 | 217.6 | YES
25 | OK | 33 | 51 | 51 | 86 | 133 | 15.52 | 50 | 58.3 | 31.2 | 39.4 | 41.8 | 223.7 | 217.4 | 217.4 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 67-016149
TR_B (available) | 63-022545
TR_A Rated kVA | 100
TR_B Rated kVA | 160
TR_A Baseline Loading% | 58.3
TR_B Baseline Loading% | 31.2
Total Scenarios Evaluated | 27
Feasible Scenarios | 25
--- Optimal Solution ---
Switch Parent Node | 15
Switch Child Node | 37
Tie Node (TR_A side) | 37
Tie Node (TR_B side) | 104
Tie Line Distance (m) | 84.4
Load Transferred (kW) | 18.23
TR_A Loading After (%) | 35
TR_B Loading After (%) | 44.6
Minimum Voltage (V) | 220.8