## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 25 | 46 | 49 | 8 | 19.5 | 13.03 | 50 | 58.3 | 21 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | ** OPTIMAL ** | 46 | 43 | 49 | 8 | 19.5 | 13.03 | 50 | 58.3 | 21 | 43.3 | 36.6 | 216.8 | 217.5 | 216.8 | YES
2 | OK | 43 | 29 | 49 | 8 | 19.5 | 12.97 | 50 | 58.3 | 21 | 43.4 | 36.6 | 216.7 | 217.5 | 216.7 | YES
3 | OK | 29 | 30 | 49 | 8 | 19.5 | 9.97 | 50 | 58.3 | 21 | 46.9 | 33 | 216.8 | 216.9 | 216.8 | YES
4 | OK | 30 | 20 | 49 | 8 | 19.5 | 8.84 | 50 | 58.3 | 21 | 46.9 | 31.6 | 216.8 | 216.8 | 216.8 | YES
5 | OK | 20 | 21 | 49 | 8 | 19.5 | 6.78 | 50 | 58.3 | 21 | 50.5 | 29 | 216.4 | 221.8 | 216.4 | YES
6 | OK | 21 | 28 | 49 | 8 | 19.5 | 5.6 | 50 | 58.3 | 21 | 51.9 | 27.6 | 216.4 | 223.1 | 216.4 | YES
7 | OK | 28 | 27 | 49 | 8 | 19.5 | 2.36 | 50 | 58.3 | 21 | 55.6 | 23.8 | 215.9 | 224.1 | 215.9 | YES
8 | OK | 27 | 23 | 49 | 8 | 19.5 | 1.52 | 50 | 58.3 | 21 | 56.6 | 22.8 | 215.9 | 224.1 | 215.9 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 67-016149
TR_B (available) | 64-021026
TR_A Rated kVA | 100
TR_B Rated kVA | 100
TR_A Baseline Loading% | 58.3
TR_B Baseline Loading% | 21
Total Scenarios Evaluated | 9
Feasible Scenarios | 8
--- Optimal Solution ---
Switch Parent Node | 46
Switch Child Node | 43
Tie Node (TR_A side) | 49
Tie Node (TR_B side) | 8
Tie Line Distance (m) | 19.5
Load Transferred (kW) | 13.03
TR_A Loading After (%) | 43.3
TR_B Loading After (%) | 36.6
Minimum Voltage (V) | 216.8