## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 25 | 24 | 8 | 10 | 4 | 36.58 | 50 | 58.3 | 26.3 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 24 | 47 | 8 | 10 | 4 | 36.58 | 50 | 58.3 | 26.3 | 15 | 53.1 | 228.5 | 220.6 | 220.6 | YES
2 | OK | 47 | 48 | 8 | 10 | 4 | 36.58 | 50 | 58.3 | 26.3 | 15 | 53.1 | 228.5 | 220.6 | 220.6 | YES
3 | OK | 48 | 14 | 8 | 10 | 4 | 36.58 | 50 | 58.3 | 26.3 | 15 | 53.1 | 228.5 | 220.6 | 220.6 | YES
4 | OK | 14 | 13 | 8 | 10 | 4 | 34.45 | 50 | 58.3 | 26.3 | 17.4 | 51.5 | 228.2 | 220.5 | 220.5 | YES
5 | OK | 13 | 12 | 8 | 10 | 4 | 33.93 | 50 | 58.3 | 26.3 | 18 | 51.1 | 228.2 | 220.8 | 220.8 | YES
6 | OK | 12 | 26 | 8 | 10 | 4 | 32.26 | 50 | 58.3 | 26.3 | 19.9 | 49.9 | 228.2 | 221.8 | 221.8 | YES
7 | OK | 26 | 11 | 8 | 10 | 4 | 27.5 | 50 | 58.3 | 26.3 | 25.4 | 46.2 | 227.5 | 221.5 | 221.5 | YES
8 | OK | 11 | 10 | 8 | 10 | 4 | 27.22 | 50 | 58.3 | 26.3 | 25.7 | 46.2 | 227.3 | 221.5 | 221.5 | YES
9 | OK | 10 | 6 | 8 | 10 | 4 | 26.38 | 50 | 58.3 | 26.3 | 26.7 | 45.5 | 227.5 | 222 | 222 | YES
10 | OK | 6 | 5 | 8 | 10 | 4 | 24.83 | 50 | 58.3 | 26.3 | 28.5 | 44.4 | 226.6 | 221.9 | 221.9 | YES
11 | OK | 5 | 2 | 8 | 10 | 4 | 23.03 | 50 | 58.3 | 26.3 | 28.5 | 43.1 | 226.6 | 222.2 | 222.2 | YES
12 | OK | 2 | 3 | 8 | 10 | 4 | 22.75 | 50 | 58.3 | 26.3 | 30.9 | 42.9 | 226.6 | 222.4 | 222.4 | YES
13 | OK | 3 | 4 | 8 | 10 | 4 | 2.39 | 50 | 58.3 | 26.3 | 54.5 | 28 | 217.4 | 223.4 | 217.4 | YES
14 | OK | 3 | 15 | 39 | 30 | 29.6 | 19.66 | 50 | 58.3 | 26.3 | 34.5 | 40.6 | 224.8 | 222.8 | 222.8 | YES
15 | OK | 4 | 31 | 8 | 10 | 4 | 2.39 | 50 | 58.3 | 26.3 | 55.4 | 27.3 | 217.4 | 223.4 | 217.4 | YES
16 | OK | 15 | 36 | 39 | 30 | 29.6 | 0.45 | 50 | 58.3 | 26.3 | 57.8 | 26.6 | 216.2 | 223.6 | 216.2 | YES
17 | OK | 15 | 37 | 37 | 10 | 47.9 | 18.23 | 95 | 58.3 | 26.3 | 35 | 39.5 | 224.6 | 222.8 | 222.8 | YES
18 | OK | 31 | 9 | 8 | 10 | 4 | 1.38 | 50 | 58.3 | 26.3 | 56.6 | 27.3 | 216.1 | 223.4 | 216.1 | YES
| NG | 36 | 38 | 39 | 30 | 29.6 | 0.22 | 50 | 58.3 | 26.3 | 58.1 | 23.7 | 215.9 | 7.9 | 7.9 | NO
19 | OK | 37 | 35 | 35 | 10 | 49.6 | 18.23 | 50 | 58.3 | 26.3 | 35 | 39.6 | 224.6 | 222.8 | 222.8 | YES
20 | OK | 9 | 7 | 8 | 10 | 4 | 0.16 | 50 | 58.3 | 26.3 | 58.1 | 26.4 | 216.2 | 223.6 | 216.2 | YES
21 | OK | 35 | 17 | 52 | 39 | 61.9 | 17.2 | 50 | 58.3 | 26.3 | 37.4 | 34.7 | 224.1 | 221.2 | 221.2 | YES
22 | OK | 17 | 16 | 52 | 39 | 61.9 | 16.89 | 50 | 58.3 | 26.3 | 37.8 | 34.5 | 224.2 | 221.5 | 221.5 | YES
23 | OK | 16 | 34 | 52 | 39 | 61.9 | 16.33 | 50 | 58.3 | 26.3 | 37.8 | 34.5 | 224.2 | 221.5 | 221.5 | YES
24 | OK | 34 | 33 | 52 | 39 | 61.9 | 15.52 | 50 | 58.3 | 26.3 | 37.8 | 34 | 224.2 | 222.1 | 222.1 | YES
25 | ** OPTIMAL ** | 33 | 51 | 52 | 39 | 61.9 | 15.52 | 50 | 58.3 | 26.3 | 39.4 | 33.1 | 223.7 | 222.9 | 222.9 | YES
26 | OK | 51 | 45 | 45 | 39 | 78.8 | 14.25 | 50 | 58.3 | 26.3 | 40.9 | 33.1 | 221.6 | 222.9 | 221.6 | YES
27 | OK | 45 | 32 | 32 | 39 | 80.4 | 10 | 50 | 58.3 | 26.3 | 46.1 | 30.5 | 218.9 | 223.2 | 218.9 | YES
28 | OK | 32 | 19 | 19 | 39 | 84 | 7.51 | 50 | 58.3 | 26.3 | 49 | 30.5 | 219.7 | 223.2 | 219.7 | YES
29 | OK | 19 | 18 | 41 | 29 | 86.3 | 3.46 | 95 | 58.3 | 26.3 | 54.1 | 28.8 | 215 | 223.3 | 215 | YES
30 | OK | 18 | 42 | 41 | 29 | 86.3 | 2.07 | 95 | 58.3 | 26.3 | 55.8 | 26.3 | 215.1 | 223.6 | 215.1 | YES
31 | OK | 42 | 40 | 41 | 29 | 86.3 | 2.07 | 95 | 58.3 | 26.3 | 55.8 | 26.3 | 215.1 | 223.6 | 215.1 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 67-016149
TR_B (available) | 66-011082
TR_A Rated kVA | 100
TR_B Rated kVA | 160
TR_A Baseline Loading% | 58.3
TR_B Baseline Loading% | 26.3
Total Scenarios Evaluated | 33
Feasible Scenarios | 31
--- Optimal Solution ---
Switch Parent Node | 33
Switch Child Node | 51
Tie Node (TR_A side) | 52
Tie Node (TR_B side) | 39
Tie Line Distance (m) | 61.9
Load Transferred (kW) | 15.52
TR_A Loading After (%) | 39.4
TR_B Loading After (%) | 33.1
Minimum Voltage (V) | 222.9